{"text_format":"3","workbook":"xls","n_sheets":18,"sheets":["Sheet2","夹角计算","镇墩转弯处水头","钢管每米自重计算","各镇墩钢管上下游转弯处及伸缩处水头计算","A1计算","A3计算","A4计算","A6计算","A7计算","A8计算","钢管自重计算","水重计算","上管段轴向合力","下管段轴向合力","上下管段法向合力","镇墩上下游面作用的弯矩","体积计算"],"not_rendered":{"images":6,"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet2","index":0,"n_rows":33,"n_cols":14,"rows_kept":33,"merged":[[1,0,2,0],[1,1,2,1]],"flags":["formulas_cached_only"]}
["支墩"]
["编号","θ","                  与水平线夹角",null,"qw1","qs1","a3","X温升","Y温升","Q0升","X温降","Y温降","Q0降","V"]
[null,null,"上游α1","下游α2"]
[{"v":0,"d":"0.00"},{"v":4.861,"d":"4.86"},{"v":0,"d":"0.00"},{"v":4.861,"d":"4.86"},2.77,0.89,10.98,{"v":10.630560383258574,"d":"10.63"},{"v":4.576809580689733,"d":"4.58"},{"v":27.314871569085987,"d":"27.31"},{"v":-11.2505340550207,"d":"-11.25"},{"v":2.7168885654033588,"d":"2.72"},{"v":-36.468490730465454,"d":"-36.47"},1.2415850713220904]
[{"v":1,"d":"1.00"},{"v":2.6,"d":"2.60"},{"v":4.861,"d":"4.86"},{"v":7.461,"d":"7.46"},2.77,0.89,10.98,{"v":10.412115476714856,"d":"10.41"},{"v":5.054092529777722,"d":"5.05"},{"v":26.182253900366845,"d":"26.18"},{"v":-11.362147899238519,"d":"-11.36"},{"v":2.2039952622067362,"d":"2.20"},{"v":-36.29043895992229,"d":"-36.29"},1.1901024500166748]
["1'",{"v":3.953,"d":"3.95"},{"v":7.461,"d":"7.46"},{"v":11.414,"d":"11.41"},2.77,0.89,10.98,{"v":10.039126085088402,"d":"10.04"},{"v":5.7595093061560085,"d":"5.76"},{"v":24.357868949109196,"d":"24.36"},{"v":-11.487006451764326,"d":"-11.49"},{"v":1.4158682061282337,"d":"1.42"},{"v":-35.876887561421206,"d":"-35.88"},1.1071758613231453]
[{"v":2,"d":"2.00"},{"v":0.981,"d":"0.98"},{"v":11.414,"d":"11.41"},{"v":12.395,"d":"12.40"},2.77,0.89,10.98,{"v":9.93909844590969,"d":"9.94"},{"v":5.9304571562836195,"d":"5.93"},{"v":23.886838181445448,"d":"23.89"},{"v":-11.509553050497924,"d":"-11.51"},{"v":1.219093342518919,"d":"1.22"},{"v":-35.74775249401269,"d":"-35.75"},1.085765371883884]
[{"v":3,"d":"3.00"},{"v":-8.027,"d":"-8.03"},{"v":12.395,"d":"12.40"},{"v":4.368,"d":"4.37"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":11.544079305678682,"d":"11.54"},{"v":4.852858228322891,"d":"4.85"},{"v":29.77937968871316,"d":"29.78"},{"v":-12.14697838153668,"d":"-12.15"},{"v":3.044161000748897,"d":"3.04"},{"v":-39.48509614535894,"d":"-39.49"},1.35360816766878]
[{"v":4,"d":"4.00"},{"v":0,"d":"0.00"},{"v":4.368,"d":"4.37"},{"v":4.368,"d":"4.37"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":11.544079305678682,"d":"11.54"},{"v":4.852858228322891,"d":"4.85"},{"v":29.77937968871316,"d":"29.78"},{"v":-12.14697838153668,"d":"-12.15"},{"v":3.044161000748897,"d":"3.04"},{"v":-39.48509614535894,"d":"-39.49"},1.35360816766878]
[{"v":5,"d":"5.00"},{"v":7.392,"d":"7.39"},{"v":4.368,"d":"4.37"},{"v":11.760000000000002,"d":"11.76"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":10.824195092402718,"d":"10.82"},{"v":6.297046974702102,"d":"6.30"},{"v":26.17553830250605,"d":"26.18"},{"v":-12.437584258743435,"d":"-12.44"},{"v":1.45687947567995,"d":"1.46"},{"v":-38.76963225191025,"d":"-38.77"},1.189797195568457]
[{"v":6,"d":"6.00"},{"v":-5.822,"d":"-5.82"},{"v":11.760000000000002,"d":"11.76"},{"v":5.9380000000000015,"d":"5.94"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":11.406857637193054,"d":"11.41"},{"v":5.167165455528826,"d":"5.17"},{"v":29.053407456050337,"d":"29.05"},{"v":-12.22578538307174,"d":"-12.23"},{"v":2.7103822178927732,"d":"2.71"},{"v":-39.38773836710799,"d":"-39.39"},1.3206094298204698]
[{"v":7,"d":"7.00"},{"v":0,"d":"0.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":11.406857637193054,"d":"11.41"},{"v":5.167165455528826,"d":"5.17"},{"v":29.053407456050337,"d":"29.05"},{"v":-12.22578538307174,"d":"-12.23"},{"v":2.7103822178927732,"d":"2.71"},{"v":-39.38773836710799,"d":"-39.39"},1.3206094298204698]
[{"v":8,"d":"8.00"},{"v":0,"d":"0.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":11.406857637193054,"d":"11.41"},{"v":5.167165455528826,"d":"5.17"},{"v":29.053407456050337,"d":"29.05"},{"v":-12.22578538307174,"d":"-12.23"},{"v":2.7103822178927732,"d":"2.71"},{"v":-39.38773836710799,"d":"-39.39"},1.3206094298204698]
[{"v":9,"d":"9.00"},{"v":7.809,"d":"7.81"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.747000000000002,"d":"13.75"},2.77,1.19,{"v":11.879999999999999,"d":"11.88"},{"v":10.599468076595038,"d":"10.60"},{"v":6.668378850458533,"d":"6.67"},{"v":25.130025379326582,"d":"25.13"},{"v":-12.48060177155115,"d":"-12.48"},{"v":1.0249777655901968,"d":"1.02"},{"v":-38.466783080243644,"d":"-38.47"},1.142273880878481]
[{"v":10,"d":"10.00"},{"v":19.2,"d":"19.20"},{"v":13.747000000000002,"d":"13.75"},{"v":32.947,"d":"32.95"},2.77,1.49,12.78,{"v":8.41085546083266,"d":"8.41"},{"v":10.522999117028444,"d":"10.52"},{"v":14.709567265469538,"d":"14.71"},{"v":-13.042483838883193,"d":"-13.04"},{"v":-3.371886017123159,"d":"-3.37"},{"v":-35.75556549952642,"d":"-35.76"},0.668616693884979]
[{"v":11,"d":"11.00"},{"v":2.302,"d":"2.30"},{"v":32.947,"d":"32.95"},{"v":35.249,"d":"35.25"},2.77,1.49,12.78,{"v":7.981615045619406,"d":"7.98"},{"v":10.852180484287105,"d":"10.85"},{"v":13.092664652571111,"d":"13.09"},{"v":-12.896600327067787,"d":"-12.90"},{"v":-3.892775360058042,"d":"-3.89"},{"v":-34.79702562114532,"d":"-34.80"},0.5951211205714141]
[{"v":12,"d":"12.00"},1.69,{"v":35.249,"d":"35.25"},{"v":36.939,"d":"36.94"},2.77,1.79,{"v":13.680000000000001,"d":"13.68"},{"v":8.197572742657528,"d":"8.20"},{"v":11.863212091539053,"d":"11.86"},{"v":12.72950613643353,"d":"12.73"},{"v":-13.675985449049456,"d":"-13.68"},{"v":-4.572026027636726,"d":"-4.57"},{"v":-36.455930319511644,"d":"-36.46"},0.5786139152924332]
[{"v":13,"d":"13.00"},1.68,{"v":36.939,"d":"36.94"},{"v":38.619,"d":"38.62"},2.77,2.09,{"v":14.579999999999998,"d":"14.58"},{"v":8.36264376783838,"d":"8.36"},{"v":12.89426962694025,"d":"12.89"},{"v":12.19366167657489,"d":"12.19"},{"v":-14.426676790434852,"d":"-14.43"},{"v":-5.2978294408491715,"d":"-5.30"},{"v":-37.982200930455384,"d":"-37.98"},0.5542573489352223]
[{"v":14,"d":"14.00"},{"v":-7.753,"d":"-7.75"},{"v":38.619,"d":"38.62"},{"v":30.866,"d":"30.87"},2.77,{"v":2.4,"d":"2.40"},15.51,{"v":10.66432027753022,"d":"10.66"},{"v":12.391984224419339,"d":"12.39"},{"v":19.60097660817132,"d":"19.60"},{"v":-15.966646756675779,"d":"-15.97"},{"v":-3.5149952130173396,"d":"-3.51"},{"v":-44.38494505701,"d":"-44.38"},0.8909534821896054]
[{"v":15,"d":"15.00"},{"v":-14.872,"d":"-14.87"},{"v":30.866,"d":"30.87"},{"v":15.994,"d":"15.99"},2.77,{"v":2.4,"d":"2.40"},15.51,{"v":13.486399781404494,"d":"13.49"},{"v":9.241537801477241,"d":"9.24"},{"v":31.217661542736238,"d":"31.22"},{"v":-16.33404250600994,"d":"-16.33"},{"v":0.698609627660904,"d":"0.70"},{"v":-49.700737145690724,"d":"-49.70"},1.4189846155789199]
[{"v":16,"d":"16.00"},{"v":16.677,"d":"16.68"},{"v":15.994,"d":"15.99"},{"v":32.671,"d":"32.67"},2.77,{"v":2.4,"d":"2.40"},15.51,{"v":10.268909480861065,"d":"10.27"},{"v":12.721576084506264,"d":"12.72"},{"v":18.085152358076932,"d":"18.09"},{"v":-15.848073235392611,"d":"-15.85"},{"v":-4.015915179088371,"d":"-4.02"},{"v":-43.52830452708946,"d":"-43.53"},0.8220523799125878]
[{"v":17,"d":"17.00"},{"v":5.878,"d":"5.88"},{"v":32.671,"d":"32.67"},{"v":38.549,"d":"38.55"},2.77,{"v":2.7,"d":"2.70"},{"v":16.410000000000004,"d":"16.41"},{"v":9.429990590872576,"d":"9.43"},{"v":14.501181933072035,"d":"14.50"},{"v":13.788789839545691,"d":"13.79"},{"v":-16.24470163254128,"d":"-16.24"},{"v":-5.942951191934084,"d":"-5.94"},{"v":-42.79115370568975,"d":"-42.79"},0.6267631745248041]
[{"v":18,"d":"18.00"},{"v":-25.726,"d":"-25.73"},{"v":38.549,"d":"38.55"},{"v":12.823,"d":"12.82"},2.77,{"v":2.7,"d":"2.70"},{"v":16.410000000000004,"d":"16.41"},{"v":14.78774703905013,"d":"14.79"},{"v":8.973936567029222,"d":"8.97"},{"v":35.38930455012117,"d":"35.39"},{"v":-17.214559571457638,"d":"-17.21"},{"v":1.693498969806699,"d":"1.69"},{"v":-53.33717768417961,"d":"-53.34"},1.608604752278235]
[{"v":19,"d":"19.00"},-3.99,{"v":12.823,"d":"12.82"},{"v":8.833,"d":"8.83"},2.77,{"v":2.7,"d":"2.70"},{"v":16.410000000000004,"d":"16.41"},{"v":15.376052643089865,"d":"15.38"},{"v":7.923762055799589,"d":"7.92"},{"v":38.204395873470006,"d":"38.20"},{"v":-17.055099347951646,"d":"-17.06"},{"v":2.886621941214246,"d":"2.89"},{"v":-54.05191998506918,"d":"-54.05"},1.736563448794091]
[{"v":20,"d":"20.00"},{"v":7.849,"d":"7.85"},{"v":8.833,"d":"8.83"},{"v":16.682000000000002,"d":"16.68"},2.77,3.01,{"v":17.339999999999996,"d":"17.34"},{"v":14.9525539666158,"d":"14.95"},{"v":10.512142021274348,"d":"10.51"},{"v":34.34551987857305,"d":"34.35"},{"v":-18.26932838605725,"d":"-18.27"},{"v":0.5618187629500042,"d":"0.56"},{"v":-55.36980392112175,"d":"-55.37"},1.5611599944805932]
[{"v":21,"d":"21.00"},{"v":11.188,"d":"11.19"},{"v":16.682000000000002,"d":"16.68"},{"v":27.870000000000005,"d":"27.87"},2.77,3.01,{"v":17.339999999999996,"d":"17.34"},{"v":12.63004152140299,"d":"12.63"},{"v":13.212344650652899,"d":"13.21"},{"v":24.677779913556076,"d":"24.68"},{"v":-18.03144000751413,"d":"-18.03"},{"v":-2.9918508076805237,"d":"-2.99"},{"v":-51.10246921486187,"d":"-51.10"},1.1217172687980035]
[{"v":22,"d":"22.00"},{"v":1.297,"d":"1.30"},{"v":27.870000000000005,"d":"27.87"},{"v":29.167000000000005,"d":"29.17"},2.77,3.01,{"v":17.339999999999996,"d":"17.34"},{"v":12.327899266539012,"d":"12.33"},{"v":13.494698947144645,"d":"13.49"},{"v":23.48899885247239,"d":"23.49"},{"v":-17.959138781517996,"d":"-17.96"},{"v":-3.3990195977923072,"d":"-3.40"},{"v":-50.47839674676169,"d":"-50.48"},1.0676817660214721]
[{"v":23,"d":"23.00"},{"v":0,"d":"0.00"},{"v":29.167000000000005,"d":"29.17"},{"v":29.167000000000005,"d":"29.17"},2.77,3.31,{"v":18.240000000000002,"d":"18.24"},{"v":12.96775562985419,"d":"12.97"},{"v":14.195115847515476,"d":"14.20"},{"v":24.7081510420471,"d":"24.71"},{"v":-18.89127401239264,"d":"-18.89"},{"v":-3.575439300099868,"d":"-3.58"},{"v":-53.09838273707805,"d":"-53.10"},1.1230977746385045]
[{"v":24,"d":"24.00"},{"v":1.037,"d":"1.04"},{"v":29.167000000000005,"d":"29.17"},{"v":30.204000000000004,"d":"30.20"},2.77,3.62,19.17,{"v":13.356844442470294,"d":"13.36"},{"v":15.162971560339038,"d":"15.16"},{"v":24.907561767071847,"d":"24.91"},{"v":-19.78325849017966,"d":"-19.78"},{"v":-4.116270582789054,"d":"-4.12"},{"v":-55.233504887749916,"d":"-55.23"},1.1321618985032658]
[{"v":25,"d":"25.00"},{"v":-4.691,"d":"-4.69"},{"v":30.204000000000004,"d":"30.20"},{"v":25.513000000000005,"d":"25.51"},2.77,3.62,19.17,{"v":14.5515778429182,"d":"14.55"},{"v":14.020434454092078,"d":"14.02"},{"v":29.634299074662522,"d":"29.63"},{"v":-20.053522946789805,"d":"-20.05"},{"v":-2.485400857522743,"d":"-2.49"},{"v":-57.67516798284667,"d":"-57.68"},1.3470135943028418]
[{"v":26,"d":"26.00"},{"v":-3.857,"d":"-3.86"},{"v":25.513000000000005,"d":"25.51"},{"v":21.656000000000006,"d":"21.66"},2.77,3.62,19.17,{"v":15.461280950721576,"d":"15.46"},{"v":13.010372452887509,"d":"13.01"},{"v":33.373470399277224,"d":"33.37"},{"v":-20.175248232309766,"d":"-20.18"},{"v":-1.131529391877061,"d":"-1.13"},{"v":-59.394215305052235,"d":"-59.39"},1.5169759272398737]
[{"v":27,"d":"27.00"},{"v":11.647,"d":"11.65"},{"v":21.656000000000006,"d":"21.66"},{"v":33.303000000000004,"d":"33.30"},2.77,3.62,19.17,{"v":12.518015292461737,"d":"12.52"},{"v":15.862543715863929,"d":"15.86"},{"v":21.691502161521278,"d":"21.69"},{"v":-19.531938463487744,"d":"-19.53"},{"v":-5.179225797214099,"d":"-5.18"},{"v":-53.41658959324913,"d":"-53.42"},0.9859773709782399]
[{"v":28,"d":"28.00"},{"v":-29.943,"d":"-29.94"},{"v":33.303000000000004,"d":"33.30"},{"v":3.360000000000003,"d":"3.36"},0.69,1.85,7.62,{"v":7.458121769171389,"d":"7.46"},{"v":2.982016042245886,"d":"2.98"},{"v":19.392349265268283,"d":"19.39"},{"v":-7.755707040684643,"d":"-7.76"},{"v":2.089260227706125,"d":"2.09"},{"v":-25.356381349760053,"d":"-25.36"},0.8814704211485583]

{"sheet":"夹角计算","index":1,"n_rows":35,"n_cols":7,"rows_kept":35,"merged":[[0,0,0,6],[1,0,2,0],[1,1,2,1],[1,2,2,2],[1,3,2,3]],"flags":["formulas_cached_only"]}
["                    各镇墩转弯处夹角计算"]
["编号","桩号","高程","θ","                  与水平线夹角",null,"两轴线"]
[{"$nulls":4},"上游α1","下游α2","水平夹角"]
[0,"0+000",1284.365,4.861,0,4.861,11.23]
[1,"0+72.484",1278.2,2.6,4.861,7.461,26.957]
["1'","0+148.623",1268.228,3.953,7.461,11.414,4.698]
[2,"0+227.082",1252.387,0.981,11.414,12.395,55.788]
[3,"0+313.838",1233.32,-8.027,12.395,4.368,43.734]
[4,"0+384.103",1227.952,0,4.368,4.368,0]
[5,"0+460.443",1222.12,7.392,4.368,11.760000000000002,0]
[6,"0+547.034",1204.093,-5.822,11.760000000000002,5.9380000000000015,0]
[7,"0+656.488",1192.707,0,5.9380000000000015,5.9380000000000015,0]
[8,"0+765.953",1182.32,0,5.9380000000000015,5.9380000000000015,0]
[9,"0+852.558",1172.311,7.809,5.9380000000000015,13.747000000000002,0]
[10,"0+956.557",1146.866,19.2,13.747000000000002,32.947,34.87]
[11,"1+033.535",1096.975,2.302,32.947,35.249,2.246]
[12,"1+110.809",1042.362,1.69,35.249,36.939,0]
[13,"1+163.99",1002.373,-1.68,36.939,35.259,0]
[14,"1+235.37",951.907,-7.753,35.259,27.506,0]
[15,"1+370.184",912.95,-14.872,27.506,12.634,0]
[16,"1+403.046",892.134,16.677,12.634,29.311,0]
[17,"1+487.287",844.836,5.878,29.311,35.189,0]
[18,"1+593.986",769.597,-25.726,35.189,9.463000000000001,0]
[19,"1+692.107",753.241,-3.99,9.463000000000001,5.473000000000001,0]
[20,"1+791.637",743.705,7.849,5.473000000000001,13.322000000000001,0]
[21,"1+902.934",717.576,11.188,13.322000000000001,24.51,0]
[22,"1+962.576",689.948,1.297,24.51,25.807000000000002,0]
[23,"2+030.337",657.181,0,25.807000000000002,25.807000000000002,0]
[24,"2+128.885",609.526,1.037,25.807000000000002,26.844,0]
[25,"2+214.830",566.029,-5.686,26.844,21.158]
[26,"2+302.684",532.027,-1.964,21.158,19.194000000000003,0]
[27,"2+403.856",496.808,10.749,19.194000000000003,29.943000000000005,26.732]
[28,"2+466.760",460.573,-29.943,29.943000000000005,0,58.31892]
["28'","2+466.76",460.573,-29.943,29.943,29.943]
[29,"2+472.798",460.573,-29.943,29.943,0,55]

{"sheet":"镇墩转弯处水头","index":2,"n_rows":33,"n_cols":5,"rows_kept":33,"merged":[[0,0,0,4]],"flags":["formulas_cached_only"]}
["各镇墩转弯处水头"]
["编号","管长（M）","高程（M）","设计情况水头（M）","校核情况水头（M）"]
[0,{"v":0,"d":"0.00"},1284.365,{"v":6.634999999999991,"d":"6.635"}]
[1,72.484,{"v":1278.2,"d":"1278.200"},{"v":16.460107606739157,"d":"16.460"}]
["1'",148.623,1268.228,{"v":30.276775851724462,"d":"30.277"}]
[2,227.082,1252.387,{"v":50.07959339376353,"d":"50.080"}]
[3,313.838,{"v":1233.32,"d":"1233.320"},{"v":73.52737115892918,"d":"73.527"}]
[4,384.103,1227.952,{"v":82.44342950266747,"d":"82.443"}]
[5,460.443,{"v":1222.12,"d":"1222.120"},{"v":92.13024732037177,"d":"92.130"}]
[6,547.034,1204.093,{"v":114.52969334673816,"d":"114.530"}]
[7,656.488,1192.707,{"v":131.44261539833616,"d":"131.443"}]
[8,765.953,{"v":1182.32,"d":"1182.320"},{"v":147.35709289918765,"d":"147.357"}]
[9,852.558,1172.311,{"v":161.7392458609675,"d":"161.739"}]
[10,956.557,1146.866,{"v":192.43571557832948,"d":"192.436"}]
[11,1033.535,1096.975,{"v":246.2137494527235,"d":"246.214"}]
[12,1110.809,1042.362,{"v":304.72872996156894,"d":"304.729"}]
[13,{"v":1163.99,"d":"1163.990"},1002.373,{"v":347.40312511959,"d":"347.403"}]
[14,{"v":1235.37,"d":"1235.370"},951.907,{"v":401.47348581945545,"d":"401.473"}]
[15,1370.184,{"v":912.95,"d":"912.950"},{"v":447.2379708767776,"d":"447.238"}]
[16,1403.046,892.134,{"v":469.7133502732329,"d":"469.713"}]
[17,1487.287,844.836,{"v":521.265132140946,"d":"521.265"}]
[18,1593.986,769.597,{"v":601.8919394022929,"d":"601.892"}]
[19,1692.107,753.241,{"v":623.2025972368613,"d":"623.203"}]
[20,1791.637,743.705,{"v":637.764403071235,"d":"637.764"}]
[21,1902.934,717.576,{"v":669.5133881204495,"d":"669.513"}]
[22,1962.576,689.948,{"v":700.1530339716876,"d":"700.153"}]
[23,2030.337,657.181,{"v":736.3416518672266,"d":"736.342"}]
[24,2128.885,609.526,{"v":788.9728712318994,"d":"788.973"}]
[25,{"v":2214.83,"d":"2214.830"},566.029,{"v":836.8096972384828,"d":"836.810"}]
[26,2302.684,532.027,{"v":875.2479189382022,"d":"875.248"}]
[27,2403.856,496.808,{"v":915.5756381974736,"d":"915.576"}]
[28,{"v":2466.76,"d":"2466.760"},460.573,{"v":954.9870000000001,"d":"954.987"}]
[29,2472.798,460.573,{"v":955.2918911446594,"d":"955.292"}]

{"sheet":"钢管每米自重计算","index":3,"n_rows":16,"n_cols":6,"rows_kept":16,"merged":[[0,0,0,5],[15,0,16,5]],"flags":["formulas_cached_only"]}
["钢管每米自重计算(不考虑加劲环)"]
["镇墩编号","桩号","δ(mm)","D(m)","qs","qw"]
["0~3","0+0009~0+360.797",{"v":0.006,"d":"0.01"},{"v":0.603,"d":"0.60"},{"v":0.89180082,"d":"0.89"},2.77]
["3~10","0+360.797~0+954.516",{"v":0.008,"d":"0.01"},{"v":0.604,"d":"0.60"},{"v":1.19103968,"d":"1.19"},2.77]
["10~12","0+954.516~1+157.903",0.01,{"v":0.605,"d":"0.61"},{"v":1.4912645,"d":"1.49"},2.77]
["12~13","1+157.903~1+258.867",{"v":0.012,"d":"0.01"},{"v":0.606,"d":"0.61"},{"v":1.7924752800000003,"d":"1.79"},2.77]
["13~15","1+258.867~1+438.293",{"v":0.014,"d":"0.01"},{"v":0.607,"d":"0.61"},{"v":2.09467202,"d":"2.09"},2.77]
["15~17","1+438.293~1+587.209",{"v":0.016,"d":"0.02"},{"v":0.608,"d":"0.61"},{"v":2.39785472,"d":"2.40"},2.77]
["17~20","1+587.209~1+916.914",{"v":0.018,"d":"0.02"},{"v":0.609,"d":"0.61"},{"v":2.70202338,"d":"2.70"},2.77]
["20~23","1+916.914.~2+238.819",0.02,0.61,{"v":3.007178,"d":"3.01"},2.77]
["23~24","2+238.819~2+350.619",{"v":0.022,"d":"0.02"},{"v":0.611,"d":"0.61"},{"v":3.3133185800000002,"d":"3.31"},2.77]
["24~26","2+350.619~2+461.101",{"v":0.024,"d":"0.02"},{"v":0.612,"d":"0.61"},{"v":3.62044512,"d":"3.62"},2.77]
["26~27","2+455.359~2+465.369",{"v":0.024,"d":"0.02"},{"v":0.312,"d":"0.31"},{"v":1.84571712,"d":"1.85"},0.69]
["28~29","2+460.59~2+472.798",0.02,0.31,{"v":1.5282380000000002,"d":"1.53"}]
[]
["管内流速:V=Q/F=0.886/(3.14/4*0.6^2)=3.13m/s           ( 26号之前管内流速)V=Q/F=0.443/(3.14/4*0.3^2)=6.27m/s"]

{"sheet":"各镇墩钢管上下游转弯处及伸缩处水头计算","index":4,"n_rows":33,"n_cols":10,"rows_kept":33,"merged":[[0,0,0,9]],"flags":["formulas_cached_only"]}
["各镇墩内钢管上.下游转弯处及伸缩节处水头计算"]
["编号","L1","L2","a1","a2","两轴线","H","H上","H下","H伸"]
[0,{"v":0,"d":"0.00"},{"v":36.242,"d":"36.24"},0,4.861,"水平夹角",{"v":6.634999999999991,"d":"6.63"},{"v":6.634999999999991,"d":"6.63"},{"v":6.6493985123240265,"d":"6.65"},{"v":9.704547242076892,"d":"9.70"}]
[1,{"v":36.242,"d":"36.24"},38.12,4.861,7.461,11.23,{"v":16.460107606739157,"d":"16.46"},{"v":16.445709094415122,"d":"16.45"},{"v":16.49408370873366,"d":"16.49"},{"v":21.407544211466206,"d":"21.41"}]
["1'",38.12,{"v":2,"d":"2.00"},7.461,11.414,26.957,{"v":30.276775851724462,"d":"30.28"},{"v":30.24279974972996,"d":"30.24"},{"v":30.356600960243167,"d":"30.36"},{"v":30.67237158032444,"d":"30.67"}]
[2,{"v":37.2295,"d":"37.23"},{"v":2,"d":"2.00"},11.414,12.395,4.698,{"v":50.07959339376353,"d":"50.08"},{"v":49.999768285244826,"d":"50.00"},{"v":50.17384547547024,"d":"50.17"},{"v":50.508679351301296,"d":"50.51"}]
[3,{"v":41.378,"d":"41.38"},{"v":35.1325,"d":"35.13"},12.395,4.368,55.788,{"v":73.52737115892918,"d":"73.53"},{"v":73.43311907722249,"d":"73.43"},{"v":73.53899449660462,"d":"73.54"},{"v":76.20178426279044,"d":"76.20"}]
[4,{"v":35.1325,"d":"35.13"},38.17,4.368,4.368,43.734,{"v":82.44342950266747,"d":"82.44"},{"v":82.43180616499204,"d":"82.43"},{"v":82.4550528403429,"d":"82.46"},{"v":85.349068104372,"d":"85.35"}]
[5,38.17,{"v":2,"d":"2.00"},4.368,11.760000000000002,0,{"v":92.13024732037177,"d":"92.13"},{"v":92.11862398269633,"d":"92.12"},{"v":92.21502107327906,"d":"92.22"},{"v":92.53766882702347,"d":"92.54"}]
[6,{"v":84.591,"d":"84.59"},{"v":54.727,"d":"54.73"},11.760000000000002,5.9380000000000015,0,{"v":114.52969334673816,"d":"114.53"},{"v":114.44491959383086,"d":"114.44"},{"v":114.5511916876326,"d":"114.55"},{"v":120.18846339076629,"d":"120.19"}]
[7,{"v":54.727,"d":"54.73"},{"v":54.7325,"d":"54.73"},5.9380000000000015,5.9380000000000015,0,{"v":131.44261539833616,"d":"131.44"},{"v":131.4211170574417,"d":"131.42"},{"v":131.4641137392306,"d":"131.46"},{"v":137.10195414218782,"d":"137.10"}]
[8,{"v":54.7325,"d":"54.73"},{"v":43.3025,"d":"43.30"},5.9380000000000015,5.9380000000000015,0,{"v":147.35709289918765,"d":"147.36"},{"v":147.3355945582932,"d":"147.34"},{"v":147.3785912400821,"d":"147.38"},{"v":151.83457000978257,"d":"151.83"}]
[9,{"v":43.3025,"d":"43.30"},{"v":2,"d":"2.00"},5.9380000000000015,13.747000000000002,0,{"v":161.7392458609675,"d":"161.74"},{"v":161.71774752007303,"d":"161.72"},{"v":161.85539828432687,"d":"161.86"},{"v":162.21427962232005,"d":"162.21"}]
[10,{"v":101.999,"d":"102.00"},{"v":2,"d":"2.00"},13.747000000000002,32.947,0,{"v":192.43571557832948,"d":"192.44"},{"v":192.3195631549701,"d":"192.32"},{"v":193.13989635721273,"d":"193.14"},{"v":193.52295228679205,"d":"193.52"}]
[11,{"v":74.987,"d":"74.99"},{"v":2,"d":"2.00"},32.947,35.249,34.87,{"v":246.2137494527235,"d":"246.21"},{"v":245.50956867384025,"d":"245.51"},{"v":247.0285714137234,"d":"247.03"},{"v":247.36750186620904,"d":"247.37"}]
[12,{"v":75.274,"d":"75.27"},{"v":2,"d":"2.00"},35.249,36.939,2.246,{"v":304.72872996156894,"d":"304.73"},{"v":303.91390800056905,"d":"303.91"},{"v":305.63143625047917,"d":"305.63"},{"v":305.93013625683034,"d":"305.93"}]
[13,{"v":51.181,"d":"51.18"},{"v":2,"d":"2.00"},36.939,35.259,0,{"v":347.40312511959,"d":"347.40"},{"v":346.5004188306798,"d":"346.50"},{"v":348.21845009653885,"d":"348.22"},{"v":348.5571624989842,"d":"348.56"}]
[14,69.38,{"v":2,"d":"2.00"},35.259,27.506,0,{"v":401.47348581945545,"d":"401.47"},{"v":400.6581608425066,"d":"400.66"},{"v":401.9539373018271,"d":"401.95"},{"v":402.3967370593483,"d":"402.40"}]
[15,{"v":132.814,"d":"132.81"},{"v":2,"d":"2.00"},27.506,12.634,0,{"v":447.2379708767776,"d":"447.24"},{"v":446.7575193944059,"d":"446.76"},{"v":447.33592369971876,"d":"447.34"},{"v":447.6751973614564,"d":"447.68"}]
[16,{"v":30.862,"d":"30.86"},{"v":2,"d":"2.00"},12.634,29.311,0,{"v":469.7133502732329,"d":"469.71"},{"v":469.6153974502917,"d":"469.62"},{"v":470.26245491224444,"d":"470.26"},{"v":470.69199768982054,"d":"470.69"}]
[17,{"v":82.241,"d":"82.24"},{"v":2,"d":"2.00"},29.311,35.189,0,{"v":521.265132140946,"d":"521.27"},{"v":520.7160275019344,"d":"520.72"},{"v":522.0769401734411,"d":"522.08"},{"v":522.4171740219799,"d":"522.42"}]
[18,{"v":104.699,"d":"104.70"},{"v":2,"d":"2.00"},35.189,9.463000000000001,0,{"v":601.8919394022929,"d":"601.89"},{"v":601.0801313697978,"d":"601.08"},{"v":601.9466911377699,"d":"601.95"},{"v":602.2205955333241,"d":"602.22"}]
[19,{"v":96.121,"d":"96.12"},{"v":2,"d":"2.00"},9.463000000000001,5.473000000000001,0,{"v":623.2025972368613,"d":"623.20"},{"v":623.1478455013843,"d":"623.15"},{"v":623.2208554204509,"d":"623.22"},{"v":623.3932541720983,"d":"623.39"}]
[20,97.53,{"v":2,"d":"2.00"},5.473000000000001,13.322000000000001,0,{"v":637.764403071235,"d":"637.76"},{"v":637.7461448876454,"d":"637.75"},{"v":637.8734178329225,"d":"637.87"},{"v":638.2250204519463,"d":"638.23"}]
[21,{"v":109.297,"d":"109.30"},{"v":2,"d":"2.00"},13.322000000000001,24.51,0,{"v":669.5133881204495,"d":"669.51"},{"v":669.404373358762,"d":"669.40"},{"v":669.8912838086732,"d":"669.89"},{"v":670.3426975615002,"d":"670.34"}]
[22,{"v":57.642,"d":"57.64"},{"v":2,"d":"2.00"},24.51,25.807000000000002,0,{"v":700.1530339716876,"d":"700.15"},{"v":699.7751382834639,"d":"699.78"},{"v":700.5736254386886,"d":"700.57"},{"v":701.0233049932132,"d":"701.02"}]
[23,{"v":65.761,"d":"65.76"},{"v":2,"d":"2.00"},25.807000000000002,25.807000000000002,0,{"v":736.3416518672266,"d":"736.34"},{"v":735.9210604002255,"d":"735.92"},{"v":736.7622433342276,"d":"736.76"},{"v":737.2119228887522,"d":"737.21"}]
[24,{"v":96.548,"d":"96.55"},{"v":2,"d":"2.00"},25.807000000000002,26.844,0,{"v":788.9728712318994,"d":"788.97"},{"v":788.5522797648983,"d":"788.55"},{"v":789.4294599069199,"d":"789.43"},{"v":789.8755730898499,"d":"789.88"}]
[25,{"v":83.945,"d":"83.95"},{"v":2,"d":"2.00"},26.844,21.158,0,{"v":836.8096972384828,"d":"836.81"},{"v":836.3531085634623,"d":"836.35"},{"v":837.0887977962702,"d":"837.09"},{"v":837.5312301383966,"d":"837.53"}]
[26,{"v":85.854,"d":"85.85"},{"v":2,"d":"2.00"},21.158,19.194000000000003,0,{"v":875.2479189382022,"d":"875.25"},{"v":874.9688183804149,"d":"874.97"},{"v":875.4765830151027,"d":"875.48"},{"v":875.9051336503678,"d":"875.91"}]
[27,{"v":51.634,"d":"51.63"},{"v":2,"d":"2.00"},19.194000000000003,29.943000000000005,26.732,{"v":915.5756381974736,"d":"915.58"},{"v":915.3469741205731,"d":"915.35"},{"v":916.150053416156,"d":"916.15"},{"v":916.5734554091912,"d":"916.57"}]
[28,{"v":60.904,"d":"60.90"},{"v":2,"d":"2.00"},29.943000000000005,0,26.732,{"v":954.9870000000001,"d":"954.99"},{"v":954.4125847813177,"d":"954.41"},{"v":954.9870000000001,"d":"954.99"},{"v":954.9870000000001,"d":"954.99"}]
[29,{"v":6,"d":"6.00"},{"v":2,"d":"2.00"},29.943,0,55,{"v":955.2918911446594,"d":"955.29"},{"v":954.717475925977,"d":"954.72"},{"v":955.2918911446594,"d":"955.29"},{"v":955.2918911446594,"d":"955.29"}]

{"sheet":"A1计算","index":5,"n_rows":37,"n_cols":9,"rows_kept":37,"merged":[[0,0,0,8],[33,0,33,7],[34,0,34,1],[34,2,34,3],[34,4,34,5],[34,6,34,7],[34,8,34,9],[35,0,35,1],[35,2,35,3],[35,4,35,5],[35,6,35,7],[35,8,35,9],[36,0,36,1],[36,2,36,3],[36,4,36,5],[36,6,36,7],[36,8,36,9]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A1计算"]
["编号","L1","L2","a1","a2","qs1","qs2","A1","A1'"]
[0,{"v":0,"d":"0.00"},{"v":36.242,"d":"36.24"},{"v":0,"d":"0.00"},{"v":4.861,"d":"4.86"},0.89,0.89,{"v":0,"d":"0.00"},{"v":2.7318970454484424,"d":"2.73"}]
[1,{"v":36.242,"d":"36.24"},38.12,{"v":4.861,"d":"4.86"},{"v":7.461,"d":"7.46"},0.89,0.89,{"v":2.7318970454484424,"d":"2.73"},{"v":4.403218578207072,"d":"4.40"}]
["1'",38.12,{"v":2,"d":"2.00"},{"v":7.461,"d":"7.46"},{"v":11.414,"d":"11.41"},0.89,0.89,{"v":4.403218578207072,"d":"4.40"},{"v":0.3520801984539817,"d":"0.35"}]
[2,{"v":37.2295,"d":"37.23"},{"v":2,"d":"2.00"},{"v":11.414,"d":"11.41"},{"v":12.395,"d":"12.40"},0.89,1.19,{"v":6.553884874171256,"d":"6.55"},{"v":0.5106122894699447,"d":"0.51"}]
[3,{"v":41.378,"d":"41.38"},{"v":35.1325,"d":"35.13"},{"v":12.395,"d":"12.40"},{"v":4.368,"d":"4.37"},1.19,1.19,{"v":10.564057656843687,"d":"10.56"},{"v":3.1825515935948903,"d":"3.18"}]
[4,{"v":35.1325,"d":"35.13"},38.17,{"v":4.368,"d":"4.37"},{"v":4.368,"d":"4.37"},1.19,1.19,{"v":3.1825515935948903,"d":"3.18"},{"v":3.4577099360283774,"d":"3.46"}]
[5,38.17,{"v":2,"d":"2.00"},{"v":4.368,"d":"4.37"},{"v":11.760000000000002,"d":"11.76"},1.19,1.19,{"v":3.4577099360283774,"d":"3.46"},{"v":0.4848315929155186,"d":"0.48"}]
[6,{"v":84.591,"d":"84.59"},{"v":54.727,"d":"54.73"},{"v":11.760000000000002,"d":"11.76"},{"v":5.9380000000000015,"d":"5.94"},1.19,1.19,{"v":20.506194638158316,"d":"20.51"},{"v":6.733936352393468,"d":"6.73"}]
[7,{"v":54.727,"d":"54.73"},{"v":54.7325,"d":"54.73"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},1.19,1.19,{"v":6.733936352393468,"d":"6.73"},{"v":6.734613105183465,"d":"6.73"}]
[8,{"v":54.7325,"d":"54.73"},{"v":43.3025,"d":"43.30"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},1.19,1.19,{"v":6.734613105183465,"d":"6.73"},{"v":5.328197761607948,"d":"5.33"}]
[9,{"v":43.3025,"d":"43.30"},{"v":2,"d":"2.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.747000000000002,"d":"13.75"},1.19,1.49,{"v":5.328197761607948,"d":"5.33"},{"v":0.7078003044153048,"d":"0.71"}]
[10,{"v":101.999,"d":"102.00"},{"v":2,"d":"2.00"},{"v":13.747000000000002,"d":"13.75"},{"v":32.947,"d":"32.95"},1.49,1.49,{"v":36.09746162502834,"d":"36.10"},{"v":1.6199826956092245,"d":"1.62"}]
[11,{"v":74.987,"d":"74.99"},{"v":2,"d":"2.00"},{"v":32.947,"d":"32.95"},{"v":35.249,"d":"35.25"},1.49,1.79,{"v":60.73882119782445,"d":"60.74"},{"v":2.0652168201391095,"d":"2.07"}]
[12,{"v":75.274,"d":"75.27"},{"v":2,"d":"2.00"},{"v":35.249,"d":"35.25"},{"v":36.939,"d":"36.94"},1.79,2.09,{"v":77.72856545957566,"d":"77.73"},{"v":2.510939157096299,"d":"2.51"}]
[13,{"v":51.181,"d":"51.18"},{"v":2,"d":"2.00"},{"v":36.939,"d":"36.94"},{"v":35.259,"d":"35.26"},2.09,2.09,{"v":64.25618849967285,"d":"64.26"},{"v":2.4119381229338135,"d":"2.41"}]
[14,69.38,{"v":2,"d":"2.00"},{"v":35.259,"d":"35.26"},{"v":27.506,"d":"27.51"},{"v":2.4,"d":"2.40"},{"v":2.4,"d":"2.40"},{"v":96.08053605884093,"d":"96.08"},{"v":2.2158029757429305,"d":"2.22"}]
[15,{"v":132.814,"d":"132.81"},{"v":2,"d":"2.00"},{"v":27.506,"d":"27.51"},{"v":12.634,"d":"12.63"},{"v":2.4,"d":"2.40"},{"v":2.4,"d":"2.40"},{"v":147.14482821016077,"d":"147.14"},{"v":1.0493435632292218,"d":"1.05"}]
[16,{"v":30.862,"d":"30.86"},{"v":2,"d":"2.00"},{"v":12.634,"d":"12.63"},{"v":29.311,"d":"29.31"},{"v":2.4,"d":"2.40"},{"v":2.7,"d":"2.70"},{"v":16.192420524190123,"d":"16.19"},{"v":2.642348024786623,"d":"2.64"}]
[17,{"v":82.241,"d":"82.24"},{"v":2,"d":"2.00"},{"v":29.311,"d":"29.31"},{"v":35.189,"d":"35.19"},{"v":2.7,"d":"2.70"},{"v":2.7,"d":"2.70"},{"v":108.65467195323833,"d":"108.65"},{"v":3.1105130787917474,"d":"3.11"}]
[18,{"v":104.699,"d":"104.70"},{"v":2,"d":"2.00"},{"v":35.189,"d":"35.19"},{"v":9.463000000000001,"d":"9.46"},{"v":2.7,"d":"2.70"},{"v":2.7,"d":"2.70"},{"v":162.8338044182086,"d":"162.83"},{"v":0.8873715537840765,"d":"0.89"}]
[19,{"v":96.121,"d":"96.12"},{"v":2,"d":"2.00"},{"v":9.463000000000001,"d":"9.46"},{"v":5.473000000000001,"d":"5.47"},{"v":2.7,"d":"2.70"},3.01,{"v":42.647520560639606,"d":"42.65"},{"v":0.5738773750634906,"d":"0.57"}]
[20,97.53,{"v":2,"d":"2.00"},{"v":5.473000000000001,"d":"5.47"},{"v":13.322000000000001,"d":"13.32"},3.01,3.01,{"v":27.985130194971116,"d":"27.99"},{"v":1.3864583159409385,"d":"1.39"}]
[21,{"v":109.297,"d":"109.30"},{"v":2,"d":"2.00"},{"v":13.322000000000001,"d":"13.32"},24.51,3.01,3.01,{"v":75.76786727869838,"d":"75.77"},{"v":2.4962214175628743,"d":"2.50"}]
[22,{"v":57.642,"d":"57.64"},{"v":2,"d":"2.00"},24.51,{"v":25.807000000000002,"d":"25.81"},3.01,3.31,{"v":71.94359747557961,"d":"71.94"},{"v":2.8805970812495056,"d":"2.88"}]
[23,{"v":65.761,"d":"65.76"},{"v":2,"d":"2.00"},{"v":25.807000000000002,"d":"25.81"},{"v":25.807000000000002,"d":"25.81"},3.31,3.62,{"v":94.71547233002435,"d":"94.72"},{"v":3.1503810979224203,"d":"3.15"}]
[24,{"v":96.548,"d":"96.55"},{"v":2,"d":"2.00"},{"v":25.807000000000002,"d":"25.81"},{"v":26.844,"d":"26.84"},3.62,3.62,{"v":152.0814971211069,"d":"152.08"},{"v":3.2677807257810376,"d":"3.27"}]
[25,{"v":83.945,"d":"83.95"},{"v":2,"d":"2.00"},{"v":26.844,"d":"26.84"},{"v":21.158,"d":"21.16"},3.62,3.62,{"v":137.1569265128446,"d":"137.16"},{"v":2.6119490976877424,"d":"2.61"}]
[26,{"v":85.854,"d":"85.85"},{"v":2,"d":"2.00"},{"v":21.158,"d":"21.16"},{"v":19.194000000000003,"d":"19.19"},3.62,3.62,{"v":112.1231389164417,"d":"112.12"},{"v":2.3791172580393516,"d":"2.38"}]
[27,{"v":51.634,"d":"51.63"},{"v":2,"d":"2.00"},{"v":19.194000000000003,"d":"19.19"},{"v":29.943000000000005,"d":"29.94"},3.62,3.62,{"v":61.421670250801945,"d":"61.42"},{"v":3.612098306417666,"d":"3.61"}]
[28,{"v":60.904,"d":"60.90"},{"v":2,"d":"2.00"},{"v":29.943000000000005,"d":"29.94"},{"v":0,"d":"0.00"},1.85,1.85,{"v":56.21323000276435,"d":"56.21"},{"v":0,"d":"0.00"}]
[29,{"v":6,"d":"6.00"},{"v":2,"d":"2.00"},{"v":29.943,"d":"29.94"},{"v":0,"d":"0.00"},1.53,1.53,{"v":4.579981001783724,"d":"4.58"},{"v":0,"d":"0.00"}]
["末端镇墩A2计算"]
["编号",null,"D",null,"H",null,"A2"]
[29,null,0.3,null,954.99,null,{"v":661.8811267350001,"d":"661.881"}]
[30,null,0.3,null,954.99,null,{"v":661.8811267350001,"d":"661.881"}]

{"sheet":"A3计算","index":6,"n_rows":33,"n_cols":6,"rows_kept":33,"merged":[[0,0,0,5]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A3计算"]
["编号","D","H上","H下","A3","A3'"]
[0,{"v":0.6,"d":"0.60"},{"v":6.634999999999991,"d":"6.63"},{"v":6.6493985123240265,"d":"6.65"},{"v":18.37549979999998,"d":"18.38"},{"v":-18.415376191911147,"d":"-18.42"}]
[1,{"v":0.6,"d":"0.60"},{"v":16.445709094415122,"d":"16.45"},{"v":16.49408370873366,"d":"16.49"},{"v":45.546062422800794,"d":"45.55"},{"v":-45.68003494966369,"d":"-45.68"}]
["1'",{"v":0.6,"d":"0.60"},{"v":30.24279974972996,"d":"30.24"},{"v":30.356600960243167,"d":"30.36"},{"v":83.75682905088215,"d":"83.76"},{"v":-84.07199922737425,"d":"-84.07"}]
[2,{"v":0.6,"d":"0.60"},{"v":49.999768285244826,"d":"50.00"},{"v":50.17384547547024,"d":"50.17"},{"v":138.47335827061985,"d":"138.47"},{"v":-138.9554615674053,"d":"-138.96"}]
[3,{"v":0.6,"d":"0.60"},{"v":73.43311907722249,"d":"73.43"},{"v":73.53899449660462,"d":"73.54"},{"v":203.37155462198615,"d":"203.37"},{"v":-203.66477447845656,"d":"-203.66"}]
[4,{"v":0.6,"d":"0.60"},{"v":82.43180616499204,"d":"82.43"},{"v":82.4550528403429,"d":"82.46"},{"v":228.2932385378222,"d":"228.29"},{"v":-228.35761974027287,"d":"-228.36"}]
[5,{"v":0.6,"d":"0.60"},{"v":92.11862398269633,"d":"92.12"},{"v":92.21502107327906,"d":"92.22"},{"v":255.1206867475979,"d":"255.12"},{"v":-255.38765656202492,"d":"-255.39"}]
[6,{"v":0.6,"d":"0.60"},{"v":114.44491959383086,"d":"114.44"},{"v":114.5511916876326,"d":"114.55"},{"v":316.9529159167227,"d":"316.95"},{"v":-317.24723435506473,"d":"-317.25"}]
[7,{"v":0.6,"d":"0.60"},{"v":131.4211170574417,"d":"131.42"},{"v":131.4641137392306,"d":"131.46"},{"v":363.9681552682437,"d":"363.97"},{"v":-364.08723371852443,"d":"-364.09"}]
[8,{"v":0.6,"d":"0.60"},{"v":147.3355945582932,"d":"147.34"},{"v":147.3785912400821,"d":"147.38"},{"v":408.0429824173019,"d":"408.04"},{"v":-408.1620608675826,"d":"-408.16"}]
[9,{"v":0.6,"d":"0.60"},{"v":161.71774752007303,"d":"161.72"},{"v":161.85539828432687,"d":"161.86"},{"v":447.8740674018919,"d":"447.87"},{"v":-448.2552884404776,"d":"-448.26"}]
[10,{"v":0.6,"d":"0.60"},{"v":192.3195631549701,"d":"192.32"},{"v":193.13989635721273,"d":"193.14"},{"v":532.6251837664266,"d":"532.63"},{"v":-534.8970801633735,"d":"-534.90"}]
[11,{"v":0.6,"d":"0.60"},{"v":245.50956867384025,"d":"245.51"},{"v":247.0285714137234,"d":"247.03"},{"v":679.9338402508272,"d":"679.93"},{"v":-684.1406879588787,"d":"-684.14"}]
[12,{"v":0.6,"d":"0.60"},{"v":303.91390800056905,"d":"303.91"},{"v":305.63143625047917,"d":"305.63"},{"v":841.683489929416,"d":"841.68"},{"v":-846.4401500669771,"d":"-846.44"}]
[13,{"v":0.6,"d":"0.60"},{"v":346.5004188306798,"d":"346.50"},{"v":348.21845009653885,"d":"348.22"},{"v":959.6259799431912,"d":"959.63"},{"v":-964.3840331733625,"d":"-964.38"}]
[14,{"v":0.6,"d":"0.60"},{"v":400.6581608425066,"d":"400.66"},{"v":401.9539373018271,"d":"401.95"},{"v":1109.6147632901054,"d":"1109.61"},{"v":-1113.2033902786643,"d":"-1113.20"}]
[15,{"v":0.6,"d":"0.60"},{"v":446.7575193944059,"d":"446.76"},{"v":447.33592369971876,"d":"447.34"},{"v":1237.2860148124194,"d":"1237.29"},{"v":-1238.8878939678973,"d":"-1238.89"}]
[16,{"v":0.6,"d":"0.60"},{"v":469.6153974502917,"d":"469.62"},{"v":470.26245491224444,"d":"470.26"},{"v":1300.5904509306342,"d":"1300.59"},{"v":-1302.3824636303627,"d":"-1302.38"}]
[17,{"v":0.6,"d":"0.60"},{"v":520.7160275019344,"d":"520.72"},{"v":522.0769401734411,"d":"522.08"},{"v":1442.1126238460572,"d":"1442.11"},{"v":-1445.8816442715417,"d":"-1445.88"}]
[18,{"v":0.6,"d":"0.60"},{"v":601.0801313697978,"d":"601.08"},{"v":601.9466911377699,"d":"601.95"},{"v":1664.6794022260276,"d":"1664.68"},{"v":-1667.079322172231,"d":"-1667.08"}]
[19,{"v":0.6,"d":"0.60"},{"v":623.1478455013843,"d":"623.15"},{"v":623.2208554204509,"d":"623.22"},{"v":1725.7954951591742,"d":"1725.80"},{"v":-1725.9976946698305,"d":"-1726.00"}]
[20,{"v":0.6,"d":"0.60"},{"v":637.7461448876454,"d":"637.75"},{"v":637.8734178329225,"d":"637.87"},{"v":1766.2251933434366,"d":"1766.23"},{"v":-1766.5776732199224,"d":"-1766.58"}]
[21,{"v":0.6,"d":"0.60"},{"v":669.404373358762,"d":"669.40"},{"v":669.8912838086732,"d":"669.89"},{"v":1853.9020239296242,"d":"1853.90"},{"v":-1855.2505126824442,"d":"-1855.25"}]
[22,{"v":0.6,"d":"0.60"},{"v":699.7751382834639,"d":"699.78"},{"v":700.5736254386886,"d":"700.57"},{"v":1938.0132499732877,"d":"1938.01"},{"v":-1940.2246441799396,"d":"-1940.22"}]
[23,{"v":0.6,"d":"0.60"},{"v":735.9210604002255,"d":"735.92"},{"v":736.7622433342276,"d":"736.76"},{"v":2038.1186583572169,"d":"2038.12"},{"v":-2040.4482976692768,"d":"-2040.45"}]
[24,{"v":0.6,"d":"0.60"},{"v":788.5522797648983,"d":"788.55"},{"v":789.4294599069199,"d":"789.43"},{"v":2183.879767763291,"d":"2183.88"},{"v":-2186.3091006230165,"d":"-2186.31"}]
[25,{"v":0.6,"d":"0.60"},{"v":836.3531085634623,"d":"836.35"},{"v":837.0887977962702,"d":"837.09"},{"v":2316.263207104338,"d":"2316.26"},{"v":-2318.3006837208145,"d":"-2318.30"}]
[26,{"v":0.6,"d":"0.60"},{"v":874.9688183804149,"d":"874.97"},{"v":875.4765830151027,"d":"875.48"},{"v":2423.208643128192,"d":"2423.21"},{"v":-2424.614887128667,"d":"-2424.61"}]
[27,{"v":0.6,"d":"0.60"},{"v":915.3469741205731,"d":"915.35"},{"v":916.150053416156,"d":"916.15"},{"v":2535.035137887445,"d":"2535.04"},{"v":-2537.2592499349757,"d":"-2537.26"}]
[28,{"v":0.3,"d":"0.30"},{"v":954.4125847813177,"d":"954.41"},{"v":954.9870000000001,"d":"954.99"},{"v":660.806641325041,"d":"660.81"},{"v":-661.2043491900001,"d":"-661.20"}]
[29,{"v":0.3,"d":"0.30"},{"v":954.717475925977,"d":"954.72"},{"v":955.2918911446594,"d":"955.29"},{"v":661.0177388068688,"d":"661.02"},{"v":-661.4154466718279,"d":"-661.42"}]

{"sheet":"A4计算","index":7,"n_rows":33,"n_cols":6,"rows_kept":33,"merged":[[0,0,0,5]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A4计算"]
["编号","D01","D02","H","A4","A4'"]
[0,null,null,6.634999999999991,0]
[1,null,null,16.460107606739157,0]
["1'",null,null,30.276775851724462,0]
[2,null,null,50.07959339376353,0]
[3,null,null,73.52737115892918,0]
[4,null,null,82.44342950266747,0]
[5,null,null,92.13024732037177,0]
[6,null,null,114.52969334673816,0]
[7,null,null,131.44261539833616,0]
[8,null,null,147.35709289918765,0]
[9,null,null,161.7392458609675,0]
[10,null,null,192.43571557832948,0]
[11,null,null,246.2137494527235,0]
[12,null,null,304.72872996156894,0]
[13,null,null,347.40312511959,0]
[14,null,null,401.47348581945545,0]
[15,null,null,447.2379708767776,0]
[16,null,null,469.7133502732329,0]
[17,null,null,521.265132140946,0]
[18,null,null,601.8919394022929,0]
[19,null,null,623.2025972368613,0]
[20,null,null,637.764403071235,0]
[21,null,null,669.5133881204495,0]
[22,null,null,700.1530339716876,0]
[23,null,null,736.3416518672266,0]
[24,null,null,788.9728712318994,0]
[25,0,0,836.8096972384828,0]
[26,0,0,875.2479189382022,0]
[27,0,0,915.5756381974736,0]
[28,0.6,0.3,954.9870000000001,1985.6371425165005]
[29,0.3,0.3,955.2918911446594,0]

{"sheet":"A6计算","index":8,"n_rows":33,"n_cols":7,"rows_kept":33,"merged":[[0,0,0,6]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A6计算"]
["编号","D1","b1","f1","H伸","A6","A6'"]
[0,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":9.704547242076892,"d":"9.70"},{"v":0,"d":"0.00"},{"v":-28.69757284959277,"d":"-28.70"}]
[1,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":21.407544211466206,"d":"21.41"},{"v":28.69757284959277,"d":"28.70"},{"v":-63.30481414689391,"d":"-63.30"}]
["1'",{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":30.67237158032444,"d":"30.67"},{"v":63.30481414689391,"d":"63.30"},{"v":-90.70207975078714,"d":"-90.70"}]
[2,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":50.508679351301296,"d":"50.51"},{"v":90.70207975078714,"d":"90.70"},{"v":-149.36054913886795,"d":"-149.36"}]
[3,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":76.20178426279044,"d":"76.20"},{"v":149.36054913886795,"d":"149.36"},{"v":-225.3383079706022,"d":"-225.34"}]
[4,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":85.349068104372,"d":"85.35"},{"v":225.3383079706022,"d":"225.34"},{"v":-252.3879825068364,"d":"-252.39"}]
[5,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":92.53766882702347,"d":"92.54"},{"v":252.3879825068364,"d":"252.39"},{"v":-273.64558348284817,"d":"-273.65"}]
[6,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":120.18846339076629,"d":"120.19"},{"v":273.64558348284817,"d":"273.65"},{"v":-355.41247806826857,"d":"-355.41"}]
[7,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":137.10195414218782,"d":"137.10"},{"v":355.41247806826857,"d":"355.41"},{"v":-405.427808085453,"d":"-405.43"}]
[8,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":151.83457000978257,"d":"151.83"},{"v":405.427808085453,"d":"405.43"},{"v":-448.99401540857633,"d":"-448.99"}]
[9,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":162.21427962232005,"d":"162.21"},{"v":448.99401540857633,"d":"448.99"},{"v":-479.6881287281447,"d":"-479.69"}]
[10,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":193.52295228679205,"d":"193.52"},{"v":479.6881287281447,"d":"479.69"},{"v":-572.2718312132132,"d":"-572.27"}]
[11,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":247.36750186620904,"d":"247.37"},{"v":572.2718312132132,"d":"572.27"},{"v":-731.4969702706161,"d":"-731.50"}]
[12,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":305.93013625683034,"d":"305.93"},{"v":731.4969702706161,"d":"731.50"},{"v":-904.6740824806703,"d":"-904.67"}]
[13,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":348.5571624989842,"d":"348.56"},{"v":904.6740824806703,"d":"904.67"},{"v":-1030.7275871348363,"d":"-1030.73"}]
[14,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":402.3967370593483,"d":"402.40"},{"v":1030.7275871348363,"d":"1030.73"},{"v":-1189.9380144320573,"d":"-1189.94"}]
[15,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":447.6751973614564,"d":"447.68"},{"v":1189.9380144320573,"d":"1189.94"},{"v":-1323.8321447427734,"d":"-1323.83"}]
[16,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":470.69199768982054,"d":"470.69"},{"v":1323.8321447427734,"d":"1323.83"},{"v":-1391.8957326373074,"d":"-1391.90"}]
[17,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":522.4171740219799,"d":"522.42"},{"v":1391.8957326373074,"d":"1391.90"},{"v":-1544.8536171137912,"d":"-1544.85"}]
[18,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":602.2205955333241,"d":"602.22"},{"v":1544.8536171137912,"d":"1544.85"},{"v":-1780.8424216753149,"d":"-1780.84"}]
[19,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":623.3932541720983,"d":"623.39"},{"v":1780.8424216753149,"d":"1780.84"},{"v":-1843.4526494942222,"d":"-1843.45"}]
[20,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":638.2250204519463,"d":"638.23"},{"v":1843.4526494942222,"d":"1843.45"},{"v":-1887.3120571189907,"d":"-1887.31"}]
[21,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":670.3426975615002,"d":"670.34"},{"v":1887.3120571189907,"d":"1887.31"},{"v":-1982.2880880063283,"d":"-1982.29"}]
[22,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":701.0233049932132,"d":"701.02"},{"v":1982.2880880063283,"d":"1982.29"},{"v":-2073.0145222106826,"d":"-2073.01"}]
[23,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":737.2119228887522,"d":"737.21"},{"v":2073.0145222106826,"d":"2073.01"},{"v":-2180.0288395690936,"d":"-2180.03"}]
[24,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":789.8755730898499,"d":"789.88"},{"v":2180.0288395690936,"d":"2180.03"},{"v":-2335.761909899125,"d":"-2335.76"}]
[25,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":837.5312301383966,"d":"837.53"},{"v":2335.761909899125,"d":"2335.76"},{"v":-2476.6857114667287,"d":"-2476.69"}]
[26,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":875.9051336503678,"d":"875.91"},{"v":2476.6857114667287,"d":"2476.69"},{"v":-2590.1621946130313,"d":"-2590.16"}]
[27,{"v":0.6,"d":"0.60"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":916.5734554091912,"d":"916.57"},{"v":2590.1621946130313,"d":"2590.16"},{"v":-2710.4235625297424,"d":"-2710.42"}]
[28,{"v":0.3,"d":"0.30"},{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":954.9870000000001,"d":"954.99"},{"v":1355.2117812648712,"d":"1355.21"},{"v":-1412.0086346784003,"d":"-1412.01"}]
[29,0.3,{"v":0.8,"d":"0.80"},{"v":0.2,"d":"0.20"},{"v":955.2918911446594,"d":"955.29"},{"v":1412.0086346784003,"d":"1412.01"},{"v":-1412.4594355048994,"d":"-1412.46"}]

{"sheet":"A7计算","index":9,"n_rows":33,"n_cols":11,"rows_kept":33,"merged":[[0,0,0,10]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A7计算"]
["编号","qs1","qs2","qw","L1","L2","f2","a1","a2","A7","A7'"]
[0,0.89,0.89,2.77,{"v":0,"d":"0.00"},{"v":36.242,"d":"36.24"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":4.861,"d":"4.86"},{"v":0,"d":"0.00"},{"v":-39.65073123160587,"d":"-39.65"}]
[1,0.89,0.89,2.77,{"v":36.242,"d":"36.24"},38.12,{"v":0.3,"d":"0.30"},{"v":4.861,"d":"4.86"},{"v":7.461,"d":"7.46"},{"v":39.65073123160587,"d":"39.65"},{"v":-41.50174599456712,"d":"-41.50"}]
["1'",0.89,0.89,2.77,38.12,{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":7.461,"d":"7.46"},{"v":11.414,"d":"11.41"},{"v":41.50174599456712,"d":"41.50"},{"v":-2.1526132536852725,"d":"-2.15"}]
[2,0.89,1.19,2.77,{"v":37.2295,"d":"37.23"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":11.414,"d":"11.41"},{"v":12.395,"d":"12.40"},{"v":40.07035756403793,"d":"40.07"},{"v":-2.3206737684637746,"d":"-2.32"}]
[3,1.19,1.19,2.77,{"v":41.378,"d":"41.38"},{"v":35.1325,"d":"35.13"},{"v":0.3,"d":"0.30"},{"v":12.395,"d":"12.40"},{"v":4.368,"d":"4.37"},{"v":48.012419595747026,"d":"48.01"},{"v":-41.61630420980469,"d":"-41.62"}]
[4,1.19,1.19,2.77,{"v":35.1325,"d":"35.13"},38.17,{"v":0.3,"d":"0.30"},{"v":4.368,"d":"4.37"},{"v":4.368,"d":"4.37"},{"v":41.61630420980469,"d":"41.62"},{"v":-45.21438359605052,"d":"-45.21"}]
[5,1.19,1.19,2.77,38.17,{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":4.368,"d":"4.37"},{"v":11.760000000000002,"d":"11.76"},{"v":45.21438359605052,"d":"45.21"},{"v":-2.3261779351146155,"d":"-2.33"}]
[6,1.19,1.19,2.77,{"v":84.591,"d":"84.59"},{"v":54.727,"d":"54.73"},{"v":0.3,"d":"0.30"},{"v":11.760000000000002,"d":"11.76"},{"v":5.9380000000000015,"d":"5.94"},{"v":98.38685885464021,"d":"98.39"},{"v":-64.66718272850157,"d":"-64.67"}]
[7,1.19,1.19,2.77,{"v":54.727,"d":"54.73"},{"v":54.7325,"d":"54.73"},{"v":0.3,"d":"0.30"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},{"v":64.66718272850157,"d":"64.67"},{"v":-64.67368170533216,"d":"-64.67"}]
[8,1.19,1.19,2.77,{"v":54.7325,"d":"54.73"},{"v":43.3025,"d":"43.30"},{"v":0.3,"d":"0.30"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},{"v":64.67368170533216,"d":"64.67"},{"v":-51.16762621925083,"d":"-51.17"}]
[9,1.19,1.49,2.77,{"v":43.3025,"d":"43.30"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.747000000000002,"d":"13.75"},{"v":51.16762621925083,"d":"51.17"},{"v":-2.4828559988157264,"d":"-2.48"}]
[10,1.49,1.49,2.77,{"v":101.999,"d":"102.00"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":13.747000000000002,"d":"13.75"},{"v":32.947,"d":"32.95"},{"v":126.62441451160262,"d":"126.62"},{"v":-2.1453339299715855,"d":"-2.15"}]
[11,1.49,1.79,2.77,{"v":74.987,"d":"74.99"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":32.947,"d":"32.95"},{"v":35.249,"d":"35.25"},{"v":80.43607770338964,"d":"80.44"},{"v":-2.234851222991869,"d":"-2.23"}]
[12,1.79,2.09,2.77,{"v":75.274,"d":"75.27"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":35.249,"d":"35.25"},{"v":36.939,"d":"36.94"},{"v":84.11309547974497,"d":"84.11"},{"v":-2.3312608072740333,"d":"-2.33"}]
[13,2.09,2.09,2.77,{"v":51.181,"d":"51.18"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":36.939,"d":"36.94"},{"v":35.259,"d":"35.26"},{"v":59.65812968854614,"d":"59.66"},{"v":-2.3815874270863127,"d":"-2.38"}]
[14,{"v":2.4,"d":"2.40"},{"v":2.4,"d":"2.40"},2.77,69.38,{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":35.259,"d":"35.26"},{"v":27.506,"d":"27.51"},{"v":87.88709357240269,"d":"87.89"},{"v":-2.7517061803403244,"d":"-2.75"}]
[15,{"v":2.4,"d":"2.40"},{"v":2.4,"d":"2.40"},2.77,{"v":132.814,"d":"132.81"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":27.506,"d":"27.51"},{"v":12.634,"d":"12.63"},{"v":182.73255231785996,"d":"182.73"},{"v":-3.026967538026804,"d":"-3.03"}]
[16,{"v":2.4,"d":"2.40"},{"v":2.7,"d":"2.70"},2.77,{"v":30.862,"d":"30.86"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":12.634,"d":"12.63"},{"v":29.311,"d":"29.31"},{"v":46.70913607929161,"d":"46.71"},{"v":-2.862239535664378,"d":"-2.86"}]
[17,{"v":2.7,"d":"2.70"},{"v":2.7,"d":"2.70"},2.77,{"v":82.241,"d":"82.24"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":29.311,"d":"29.31"},{"v":35.189,"d":"35.19"},{"v":117.69672082628705,"d":"117.70"},{"v":-2.6828214629483895,"d":"-2.68"}]
[18,{"v":2.7,"d":"2.70"},{"v":2.7,"d":"2.70"},2.77,{"v":104.699,"d":"104.70"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":35.189,"d":"35.19"},{"v":9.463000000000001,"d":"9.46"},{"v":140.44436217461669,"d":"140.44"},{"v":-3.2373836436358494,"d":"-3.24"}]
[19,{"v":2.7,"d":"2.70"},3.01,2.77,{"v":96.121,"d":"96.12"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":9.463000000000001,"d":"9.46"},{"v":5.473000000000001,"d":"5.47"},{"v":155.59027660496074,"d":"155.59"},{"v":-3.4522062826670297,"d":"-3.45"}]
[20,3.01,3.01,2.77,97.53,{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":5.473000000000001,"d":"5.47"},{"v":13.322000000000001,"d":"13.32"},{"v":168.3468393742577,"d":"168.35"},{"v":-3.374771914699241,"d":"-3.37"}]
[21,3.01,3.01,2.77,{"v":109.297,"d":"109.30"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":13.322000000000001,"d":"13.32"},24.51,{"v":184.42622298044148,"d":"184.43"},{"v":-3.1558065666199075,"d":"-3.16"}]
[22,3.01,3.31,2.77,{"v":57.642,"d":"57.64"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},24.51,{"v":25.807000000000002,"d":"25.81"},{"v":90.95350105655237,"d":"90.95"},{"v":-3.2845314269088264,"d":"-3.28"}]
[23,3.31,3.62,2.77,{"v":65.761,"d":"65.76"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":25.807000000000002,"d":"25.81"},{"v":25.807000000000002,"d":"25.81"},{"v":107.99703558247566,"d":"108.00"},{"v":-3.451999312162402,"d":"-3.45"}]
[24,3.62,3.62,2.77,{"v":96.548,"d":"96.55"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":25.807000000000002,"d":"25.81"},{"v":26.844,"d":"26.84"},{"v":166.64181479532778,"d":"166.64"},{"v":-3.4212566160206155,"d":"-3.42"}]
[25,3.62,3.62,2.77,{"v":83.945,"d":"83.95"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":26.844,"d":"26.84"},{"v":21.158,"d":"21.16"},{"v":143.5986933159253,"d":"143.60"},{"v":-3.5758038321315455,"d":"-3.58"}]
[26,3.62,3.62,2.77,{"v":85.854,"d":"85.85"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":21.158,"d":"21.16"},{"v":19.194000000000003,"d":"19.19"},{"v":153.49853110191086,"d":"153.50"},{"v":-3.621085039822526,"d":"-3.62"}]
[27,3.62,3.62,2.77,{"v":51.634,"d":"51.63"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":19.194000000000003,"d":"19.19"},{"v":29.943000000000005,"d":"29.94"},{"v":93.48555247309817,"d":"93.49"},{"v":-3.3227537525447746,"d":"-3.32"}]
[28,1.85,1.85,0.69,{"v":60.904,"d":"60.90"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":29.943000000000005,"d":"29.94"},{"v":0,"d":"0.00"},{"v":40.220441795326046,"d":"40.22"},{"v":-1.524,"d":"-1.52"}]
[29,1.53,1.53,0.69,{"v":6,"d":"6.00"},{"v":2,"d":"2.00"},{"v":0.3,"d":"0.30"},{"v":29.943,"d":"29.94"},{"v":0,"d":"0.00"},{"v":3.463151798426948,"d":"3.46"},{"v":-1.3319999999999999,"d":"-1.33"}]

{"sheet":"A8计算","index":10,"n_rows":33,"n_cols":5,"rows_kept":33,"merged":[[0,0,0,4]],"flags":["formulas_cached_only"]}
["各镇墩轴向力A8计算"]
["编号","D0","V0","A8","A8'"]
[0,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[1,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
["1'",{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[2,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[3,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[4,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[5,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[6,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[7,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[8,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[9,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[10,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[11,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[12,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[13,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[14,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[15,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[16,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[17,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[18,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[19,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[20,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[21,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[22,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[23,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[24,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[25,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[26,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[27,{"v":0.6,"d":"0.60"},3.13,{"v":2.771429046061224,"d":"2.77"},{"v":-2.771429046061224,"d":"-2.77"}]
[28,{"v":0.3,"d":"0.30"},6.27,{"v":2.7802905241683673,"d":"2.78"},{"v":-2.7802905241683673,"d":"-2.78"}]
[29,0.3,6.27,{"v":2.7802905241683673,"d":"2.78"},{"v":-2.7802905241683673,"d":"-2.78"}]

{"sheet":"钢管自重计算","index":11,"n_rows":33,"n_cols":11,"rows_kept":33,"merged":[[0,0,0,4],[0,6,0,10]],"flags":["formulas_cached_only"]}
["钢管上管段自重分力",{"$nulls":5},"钢管下管段自重分力"]
["编号","qs1","l1","a1","Qs",null,"编号","qs2","l2","a2","Qs'"]
[0,0.89,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,0,0.89,{"v":10,"d":"10.00"},{"v":4.861,"d":"4.86"},{"v":4.434010484988287,"d":"4.43"}]
[1,0.89,{"v":10,"d":"10.00"},{"v":4.861,"d":"4.86"},{"v":4.434010484988287,"d":"4.43"},null,1,0.89,{"v":10,"d":"10.00"},{"v":7.461,"d":"7.46"},{"v":4.412362113979623,"d":"4.41"}]
["1'",0.89,{"v":10,"d":"10.00"},{"v":7.461,"d":"7.46"},{"v":4.412362113979623,"d":"4.41"},null,"1'",0.89,{"v":10,"d":"10.00"},{"v":11.414,"d":"11.41"},{"v":4.362080591484273,"d":"4.36"}]
[2,0.89,{"v":10,"d":"10.00"},{"v":11.414,"d":"11.41"},{"v":4.362080591484273,"d":"4.36"},null,2,1.19,{"v":10,"d":"10.00"},{"v":12.395,"d":"12.40"},{"v":5.811451566649604,"d":"5.81"}]
[3,1.19,{"v":10,"d":"10.00"},{"v":12.395,"d":"12.40"},{"v":5.811451566649604,"d":"5.81"},null,3,1.19,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":5.9327354056789305,"d":"5.93"}]
[4,1.19,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":5.9327354056789305,"d":"5.93"},null,4,1.19,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":5.9327354056789305,"d":"5.93"}]
[5,1.19,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":5.9327354056789305,"d":"5.93"},null,5,1.19,{"v":10,"d":"10.00"},{"v":11.760000000000002,"d":"11.76"},{"v":5.825235148961263,"d":"5.83"}]
[6,1.19,{"v":10,"d":"10.00"},{"v":11.760000000000002,"d":"11.76"},{"v":5.825235148961263,"d":"5.83"},null,6,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"}]
[7,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"},null,7,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"}]
[8,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"},null,8,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"}]
[9,1.19,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.918107153643751,"d":"5.92"},null,9,1.49,{"v":10,"d":"10.00"},{"v":13.747000000000002,"d":"13.75"},{"v":7.236806412823616,"d":"7.24"}]
[10,1.49,{"v":10,"d":"10.00"},{"v":13.747000000000002,"d":"13.75"},{"v":7.236806412823616,"d":"7.24"},null,10,1.49,{"v":10,"d":"10.00"},{"v":32.947,"d":"32.95"},{"v":6.253027299799809,"d":"6.25"}]
[11,1.49,{"v":10,"d":"10.00"},{"v":32.947,"d":"32.95"},{"v":6.253027299799809,"d":"6.25"},null,11,1.79,{"v":10,"d":"10.00"},{"v":35.249,"d":"35.25"},{"v":7.3106427067899205,"d":"7.31"}]
[12,1.79,{"v":10,"d":"10.00"},{"v":35.249,"d":"35.25"},{"v":7.3106427067899205,"d":"7.31"},null,12,2.09,{"v":10,"d":"10.00"},{"v":36.939,"d":"36.94"},{"v":8.354484031554748,"d":"8.35"}]
[13,2.09,{"v":10,"d":"10.00"},{"v":36.939,"d":"36.94"},{"v":8.35448403155475,"d":"8.35"},null,13,2.09,{"v":10,"d":"10.00"},{"v":35.259,"d":"35.26"},{"v":8.534838344668028,"d":"8.53"}]
[14,{"v":2.4,"d":"2.40"},{"v":10,"d":"10.00"},{"v":35.259,"d":"35.26"},{"v":9.800771304881948,"d":"9.80"},null,14,{"v":2.4,"d":"2.40"},{"v":10,"d":"10.00"},{"v":27.506,"d":"27.51"},{"v":10.644898183134718,"d":"10.64"}]
[15,{"v":2.4,"d":"2.40"},{"v":10,"d":"10.00"},{"v":27.506,"d":"27.51"},{"v":10.644898183134718,"d":"10.64"},null,15,{"v":2.4,"d":"2.40"},{"v":10,"d":"10.00"},{"v":12.634,"d":"12.63"},{"v":11.709739025248759,"d":"11.71"}]
[16,{"v":2.4,"d":"2.40"},{"v":10,"d":"10.00"},{"v":12.634,"d":"12.63"},{"v":11.709739025248759,"d":"11.71"},null,16,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":29.311,"d":"29.31"},{"v":11.773380174122211,"d":"11.77"}]
[17,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":29.311,"d":"29.31"},{"v":11.773380174122211,"d":"11.77"},null,17,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":35.189,"d":"35.19"},{"v":11.035371648325182,"d":"11.04"}]
[18,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":35.189,"d":"35.19"},{"v":11.035371648325183,"d":"11.04"},null,18,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":9.463000000000001,"d":"9.46"},{"v":13.31647751038512,"d":"13.32"}]
[19,{"v":2.7,"d":"2.70"},{"v":10,"d":"10.00"},{"v":9.463000000000001,"d":"9.46"},{"v":13.31647751038512,"d":"13.32"},null,19,3.01,{"v":10,"d":"10.00"},{"v":5.473000000000001,"d":"5.47"},{"v":14.981460367398732,"d":"14.98"}]
[20,3.01,{"v":10,"d":"10.00"},{"v":5.473000000000001,"d":"5.47"},{"v":14.981460367398732,"d":"14.98"},null,20,3.01,{"v":10,"d":"10.00"},{"v":13.322000000000001,"d":"13.32"},{"v":14.64542021805755,"d":"14.65"}]
[21,3.01,{"v":10,"d":"10.00"},{"v":13.322000000000001,"d":"13.32"},{"v":14.64542021805755,"d":"14.65"},null,21,3.01,{"v":10,"d":"10.00"},24.51,{"v":13.69518132284591,"d":"13.70"}]
[22,3.01,{"v":10,"d":"10.00"},24.51,{"v":13.69518132284591,"d":"13.70"},null,22,3.31,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":14.901040327670254,"d":"14.90"}]
[23,3.31,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":14.901040327670254,"d":"14.90"},null,23,3.62,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":16.296606038116714,"d":"16.30"}]
[24,3.62,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":16.296606038116714,"d":"16.30"},null,24,3.62,{"v":10,"d":"10.00"},{"v":26.844,"d":"26.84"},{"v":16.15147228742127,"d":"16.15"}]
[25,3.62,{"v":10,"d":"10.00"},{"v":26.844,"d":"26.84"},{"v":16.15147228742127,"d":"16.15"},null,25,3.62,{"v":10,"d":"10.00"},{"v":21.158,"d":"21.16"},{"v":16.881077037449394,"d":"16.88"}]
[26,3.62,{"v":10,"d":"10.00"},{"v":21.158,"d":"21.16"},{"v":16.881077037449394,"d":"16.88"},null,26,3.62,{"v":10,"d":"10.00"},{"v":19.194000000000003,"d":"19.19"},{"v":17.094845910481933,"d":"17.09"}]
[27,3.62,{"v":10,"d":"10.00"},{"v":19.194000000000003,"d":"19.19"},{"v":17.094845910481933,"d":"17.09"},null,27,3.62,{"v":10,"d":"10.00"},{"v":29.943000000000005,"d":"29.94"},{"v":15.68644833621816,"d":"15.69"}]
[28,1.85,{"v":10,"d":"10.00"},{"v":29.943000000000005,"d":"29.94"},{"v":8.016555088951268,"d":"8.02"},null,28,1.85,{"v":2,"d":"2.00"},{"v":0,"d":"0.00"},1.85]
[29,1.53,{"v":4,"d":"4.00"},{"v":29.943,"d":"29.94"},{"v":2.651963088885501,"d":"2.65"},null,29,1.53,{"v":2,"d":"2.00"},{"v":0,"d":"0.00"},1.53]

{"sheet":"水重计算","index":12,"n_rows":33,"n_cols":11,"rows_kept":33,"merged":[[0,0,0,4],[0,6,0,10]],"flags":["formulas_cached_only"]}
["钢管上管段水重分力",{"$nulls":5},"钢管下管段水重分力"]
["编号","qw1","l1","a1","Qw",null,"编号","qw2","l2","a2","Qw'"]
[0,2.77,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,0,2.77,{"v":10,"d":"10.00"},{"v":4.861,"d":"4.86"},{"v":13.80023488024444,"d":"13.80"}]
[1,2.77,{"v":10,"d":"10.00"},{"v":4.861,"d":"4.86"},{"v":13.80023488024444,"d":"13.80"},null,1,2.77,{"v":10,"d":"10.00"},{"v":7.461,"d":"7.46"},{"v":13.732857365981522,"d":"13.73"}]
["1'",2.77,{"v":10,"d":"10.00"},{"v":7.461,"d":"7.46"},{"v":13.732857365981522,"d":"13.73"},null,"1'",2.77,{"v":10,"d":"10.00"},{"v":11.414,"d":"11.41"},{"v":13.576363189226331,"d":"13.58"}]
[2,2.77,{"v":10,"d":"10.00"},{"v":11.414,"d":"11.41"},{"v":13.576363189226331,"d":"13.58"},null,2,2.77,{"v":10,"d":"10.00"},{"v":12.395,"d":"12.40"},{"v":13.527496503881851,"d":"13.53"}]
[3,2.77,{"v":10,"d":"10.00"},{"v":12.395,"d":"12.40"},{"v":13.527496503881851,"d":"13.53"},null,3,2.77,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":13.809812667000537,"d":"13.81"}]
[4,2.77,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":13.809812667000537,"d":"13.81"},null,4,2.77,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":13.809812667000537,"d":"13.81"}]
[5,2.77,{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":13.809812667000537,"d":"13.81"},null,5,2.77,{"v":10,"d":"10.00"},{"v":11.760000000000002,"d":"11.76"},{"v":13.559580976993866,"d":"13.56"}]
[6,2.77,{"v":10,"d":"10.00"},{"v":11.760000000000002,"d":"11.76"},{"v":13.559580976993866,"d":"13.56"},null,6,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"}]
[7,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"},null,7,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"}]
[8,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"},null,8,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"}]
[9,2.77,{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.775762029910245,"d":"13.78"},null,9,2.77,{"v":10,"d":"10.00"},{"v":13.747000000000002,"d":"13.75"},{"v":13.453660243974104,"d":"13.45"}]
[10,2.77,{"v":10,"d":"10.00"},{"v":13.747000000000002,"d":"13.75"},{"v":13.453660243974104,"d":"13.45"},null,10,2.77,{"v":10,"d":"10.00"},{"v":32.947,"d":"32.95"},{"v":11.624755449963404,"d":"11.62"}]
[11,2.77,{"v":10,"d":"10.00"},{"v":32.947,"d":"32.95"},{"v":11.624755449963404,"d":"11.62"},null,11,2.77,{"v":10,"d":"10.00"},{"v":35.249,"d":"35.25"},{"v":11.313117484808984,"d":"11.31"}]
[12,2.77,{"v":10,"d":"10.00"},{"v":35.249,"d":"35.25"},{"v":11.313117484808984,"d":"11.31"},null,12,2.77,{"v":10,"d":"10.00"},{"v":36.939,"d":"36.94"},{"v":11.07268936239553,"d":"11.07"}]
[13,2.77,{"v":10,"d":"10.00"},{"v":36.939,"d":"36.94"},{"v":11.07268936239553,"d":"11.07"},null,13,2.77,{"v":10,"d":"10.00"},{"v":35.259,"d":"35.26"},{"v":11.311723547717914,"d":"11.31"}]
[14,2.77,{"v":10,"d":"10.00"},{"v":35.259,"d":"35.26"},{"v":11.311723547717914,"d":"11.31"},null,14,2.77,{"v":10,"d":"10.00"},{"v":27.506,"d":"27.51"},{"v":12.285986653034653,"d":"12.29"}]
[15,2.77,{"v":10,"d":"10.00"},{"v":27.506,"d":"27.51"},{"v":12.285986653034653,"d":"12.29"},null,15,2.77,{"v":10,"d":"10.00"},{"v":12.634,"d":"12.63"},{"v":13.514990458307942,"d":"13.51"}]
[16,2.77,{"v":10,"d":"10.00"},{"v":12.634,"d":"12.63"},{"v":13.514990458307942,"d":"13.51"},null,16,2.77,{"v":10,"d":"10.00"},{"v":29.311,"d":"29.31"},{"v":12.078615956414268,"d":"12.08"}]
[17,2.77,{"v":10,"d":"10.00"},{"v":29.311,"d":"29.31"},{"v":12.078615956414268,"d":"12.08"},null,17,2.77,{"v":10,"d":"10.00"},{"v":35.189,"d":"35.19"},{"v":11.321473876244724,"d":"11.32"}]
[18,2.77,{"v":10,"d":"10.00"},{"v":35.189,"d":"35.19"},{"v":11.321473876244724,"d":"11.32"},null,18,2.77,{"v":10,"d":"10.00"},{"v":9.463000000000001,"d":"9.46"},{"v":13.661719519913623,"d":"13.66"}]
[19,2.77,{"v":10,"d":"10.00"},{"v":9.463000000000001,"d":"9.46"},{"v":13.661719519913623,"d":"13.66"},null,19,2.77,{"v":10,"d":"10.00"},{"v":5.473000000000001,"d":"5.47"},{"v":13.786925321493186,"d":"13.79"}]
[20,2.77,{"v":10,"d":"10.00"},{"v":5.473000000000001,"d":"5.47"},{"v":13.786925321493186,"d":"13.79"},null,20,2.77,{"v":10,"d":"10.00"},{"v":13.322000000000001,"d":"13.32"},{"v":13.477679071102795,"d":"13.48"}]
[21,2.77,{"v":10,"d":"10.00"},{"v":13.322000000000001,"d":"13.32"},{"v":13.477679071102795,"d":"13.48"},null,21,2.77,{"v":10,"d":"10.00"},24.51,{"v":12.60320673231999,"d":"12.60"}]
[22,2.77,{"v":10,"d":"10.00"},24.51,{"v":12.60320673231999,"d":"12.60"},null,22,2.77,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":12.47005489656997,"d":"12.47"}]
[23,2.77,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":12.47005489656997,"d":"12.47"},null,23,2.77,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":12.47005489656997,"d":"12.47"}]
[24,2.77,{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":12.47005489656997,"d":"12.47"},null,24,2.77,{"v":10,"d":"10.00"},{"v":26.844,"d":"26.84"},{"v":12.358999512750527,"d":"12.36"}]
[25,2.77,{"v":10,"d":"10.00"},{"v":26.844,"d":"26.84"},{"v":12.358999512750527,"d":"12.36"},null,25,2.77,{"v":10,"d":"10.00"},{"v":21.158,"d":"21.16"},{"v":12.917288230313485,"d":"12.92"}]
[26,2.77,{"v":10,"d":"10.00"},{"v":21.158,"d":"21.16"},{"v":12.917288230313485,"d":"12.92"},null,26,2.77,{"v":10,"d":"10.00"},{"v":19.194000000000003,"d":"19.19"},{"v":13.080862754705786,"d":"13.08"}]
[27,2.77,{"v":10,"d":"10.00"},{"v":19.194000000000003,"d":"19.19"},{"v":13.080862754705786,"d":"13.08"},null,27,1.38,{"v":10,"d":"10.00"},{"v":29.943000000000005,"d":"29.94"},{"v":5.97991676905554,"d":"5.98"}]
[28,0.69,{"v":10,"d":"10.00"},{"v":29.943000000000005,"d":"29.94"},{"v":2.98995838452777,"d":"2.99"},null,28,1.38,{"v":2,"d":"2.00"},{"v":0,"d":"0.00"},1.38]
[29,0.69,{"v":4,"d":"4.00"},{"v":29.943,"d":"29.94"},{"v":1.1959833538111082,"d":"1.20"},null,29,1.38,{"v":2,"d":"2.00"},{"v":0,"d":"0.00"},1.38]

{"sheet":"上管段轴向合力","index":13,"n_rows":33,"n_cols":10,"rows_kept":33,"merged":[[0,0,0,9]],"flags":["formulas_cached_only"]}
["上游管段轴向力合力计算"]
["编号","A1","A2","A3","A4","A5","A6","A7","A8","∑A"]
[0,{"v":0,"d":"0.00"},null,{"v":18.37549979999998,"d":"18.38"},{"v":0,"d":"0.00"},null,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.771429046061224,"d":"2.77"},{"v":21.146928846061204,"d":"21.15"}]
[1,{"v":2.7318970454484424,"d":"2.73"},null,{"v":45.546062422800794,"d":"45.55"},{"v":0,"d":"0.00"},null,{"v":28.69757284959277,"d":"28.70"},{"v":39.65073123160587,"d":"39.65"},{"v":2.771429046061224,"d":"2.77"},{"v":119.39769259550911,"d":"119.40"}]
["1'",{"v":4.403218578207072,"d":"4.40"},null,{"v":83.75682905088215,"d":"83.76"},{"v":0,"d":"0.00"},null,{"v":63.30481414689391,"d":"63.30"},{"v":41.50174599456712,"d":"41.50"},{"v":2.771429046061224,"d":"2.77"},{"v":195.7380368166115,"d":"195.74"}]
[2,{"v":6.553884874171256,"d":"6.55"},null,{"v":138.47335827061985,"d":"138.47"},{"v":0,"d":"0.00"},null,{"v":90.70207975078714,"d":"90.70"},{"v":40.07035756403793,"d":"40.07"},{"v":2.771429046061224,"d":"2.77"},{"v":278.5711095056774,"d":"278.57"}]
[3,{"v":10.564057656843687,"d":"10.56"},null,{"v":203.37155462198615,"d":"203.37"},{"v":0,"d":"0.00"},null,{"v":149.36054913886795,"d":"149.36"},{"v":48.012419595747026,"d":"48.01"},{"v":2.771429046061224,"d":"2.77"},{"v":414.08001005950604,"d":"414.08"}]
[4,{"v":3.1825515935948903,"d":"3.18"},null,{"v":228.2932385378222,"d":"228.29"},{"v":0,"d":"0.00"},null,{"v":225.3383079706022,"d":"225.34"},{"v":41.61630420980469,"d":"41.62"},{"v":2.771429046061224,"d":"2.77"},{"v":501.20183135788517,"d":"501.20"}]
[5,{"v":3.4577099360283774,"d":"3.46"},null,{"v":255.1206867475979,"d":"255.12"},{"v":0,"d":"0.00"},null,{"v":252.3879825068364,"d":"252.39"},{"v":45.21438359605052,"d":"45.21"},{"v":2.771429046061224,"d":"2.77"},{"v":558.9521918325744,"d":"558.95"}]
[6,{"v":20.506194638158316,"d":"20.51"},null,{"v":316.9529159167227,"d":"316.95"},{"v":0,"d":"0.00"},null,{"v":273.64558348284817,"d":"273.65"},{"v":98.38685885464021,"d":"98.39"},{"v":2.771429046061224,"d":"2.77"},{"v":712.2629819384306,"d":"712.26"}]
[7,{"v":6.733936352393468,"d":"6.73"},null,{"v":363.9681552682437,"d":"363.97"},{"v":0,"d":"0.00"},null,{"v":355.41247806826857,"d":"355.41"},{"v":64.66718272850157,"d":"64.67"},{"v":2.771429046061224,"d":"2.77"},{"v":793.5531814634685,"d":"793.55"}]
[8,{"v":6.734613105183465,"d":"6.73"},null,{"v":408.0429824173019,"d":"408.04"},{"v":0,"d":"0.00"},null,{"v":405.427808085453,"d":"405.43"},{"v":64.67368170533216,"d":"64.67"},{"v":2.771429046061224,"d":"2.77"},{"v":887.6505143593319,"d":"887.65"}]
[9,{"v":5.328197761607948,"d":"5.33"},null,{"v":447.8740674018919,"d":"447.87"},{"v":0,"d":"0.00"},null,{"v":448.99401540857633,"d":"448.99"},{"v":51.16762621925083,"d":"51.17"},{"v":2.771429046061224,"d":"2.77"},{"v":956.1353358373882,"d":"956.14"}]
[10,{"v":36.09746162502834,"d":"36.10"},null,{"v":532.6251837664266,"d":"532.63"},{"v":0,"d":"0.00"},null,{"v":479.6881287281447,"d":"479.69"},{"v":126.62441451160262,"d":"126.62"},{"v":2.771429046061224,"d":"2.77"},{"v":1177.8066176772636,"d":"1177.81"}]
[11,{"v":60.73882119782445,"d":"60.74"},null,{"v":679.9338402508272,"d":"679.93"},{"v":0,"d":"0.00"},null,{"v":572.2718312132132,"d":"572.27"},{"v":80.43607770338964,"d":"80.44"},{"v":2.771429046061224,"d":"2.77"},{"v":1396.1519994113157,"d":"1396.15"}]
[12,{"v":77.72856545957566,"d":"77.73"},null,{"v":841.683489929416,"d":"841.68"},{"v":0,"d":"0.00"},null,{"v":731.4969702706161,"d":"731.50"},{"v":84.11309547974497,"d":"84.11"},{"v":2.771429046061224,"d":"2.77"},{"v":1737.793550185414,"d":"1737.79"}]
[13,{"v":64.25618849967285,"d":"64.26"},null,{"v":959.6259799431912,"d":"959.63"},{"v":0,"d":"0.00"},null,{"v":904.6740824806703,"d":"904.67"},{"v":59.65812968854614,"d":"59.66"},{"v":2.771429046061224,"d":"2.77"},{"v":1990.9858096581415,"d":"1990.99"}]
[14,{"v":96.08053605884093,"d":"96.08"},null,{"v":1109.6147632901054,"d":"1109.61"},{"v":0,"d":"0.00"},null,{"v":1030.7275871348363,"d":"1030.73"},{"v":87.88709357240269,"d":"87.89"},{"v":2.771429046061224,"d":"2.77"},{"v":2327.081409102246,"d":"2327.08"}]
[15,{"v":147.14482821016077,"d":"147.14"},null,{"v":1237.2860148124194,"d":"1237.29"},{"v":0,"d":"0.00"},null,{"v":1189.9380144320573,"d":"1189.94"},{"v":182.73255231785996,"d":"182.73"},{"v":2.771429046061224,"d":"2.77"},{"v":2759.872838818559,"d":"2759.87"}]
[16,{"v":16.192420524190123,"d":"16.19"},null,{"v":1300.5904509306342,"d":"1300.59"},{"v":0,"d":"0.00"},null,{"v":1323.8321447427734,"d":"1323.83"},{"v":46.70913607929161,"d":"46.71"},{"v":2.771429046061224,"d":"2.77"},{"v":2690.0955813229502,"d":"2690.10"}]
[17,{"v":108.65467195323833,"d":"108.65"},null,{"v":1442.1126238460572,"d":"1442.11"},{"v":0,"d":"0.00"},null,{"v":1391.8957326373074,"d":"1391.90"},{"v":117.69672082628705,"d":"117.70"},{"v":2.771429046061224,"d":"2.77"},{"v":3063.1311783089513,"d":"3063.13"}]
[18,{"v":162.8338044182086,"d":"162.83"},null,{"v":1664.6794022260276,"d":"1664.68"},{"v":0,"d":"0.00"},null,{"v":1544.8536171137912,"d":"1544.85"},{"v":140.44436217461669,"d":"140.44"},{"v":2.771429046061224,"d":"2.77"},{"v":3515.5826149787054,"d":"3515.58"}]
[19,{"v":42.647520560639606,"d":"42.65"},null,{"v":1725.7954951591742,"d":"1725.80"},{"v":0,"d":"0.00"},null,{"v":1780.8424216753149,"d":"1780.84"},{"v":155.59027660496074,"d":"155.59"},{"v":2.771429046061224,"d":"2.77"},{"v":3707.6471430461506,"d":"3707.65"}]
[20,{"v":27.985130194971116,"d":"27.99"},null,{"v":1766.2251933434366,"d":"1766.23"},{"v":0,"d":"0.00"},null,{"v":1843.4526494942222,"d":"1843.45"},{"v":168.3468393742577,"d":"168.35"},{"v":2.771429046061224,"d":"2.77"},{"v":3808.781241452949,"d":"3808.78"}]
[21,{"v":75.76786727869838,"d":"75.77"},null,{"v":1853.9020239296242,"d":"1853.90"},{"v":0,"d":"0.00"},null,{"v":1887.3120571189907,"d":"1887.31"},{"v":184.42622298044148,"d":"184.43"},{"v":2.771429046061224,"d":"2.77"},{"v":4004.179600353816,"d":"4004.18"}]
[22,{"v":71.94359747557961,"d":"71.94"},null,{"v":1938.0132499732877,"d":"1938.01"},{"v":0,"d":"0.00"},null,{"v":1982.2880880063283,"d":"1982.29"},{"v":90.95350105655237,"d":"90.95"},{"v":2.771429046061224,"d":"2.77"},{"v":4085.969865557809,"d":"4085.97"}]
[23,{"v":94.71547233002435,"d":"94.72"},null,{"v":2038.1186583572169,"d":"2038.12"},{"v":0,"d":"0.00"},null,{"v":2073.0145222106826,"d":"2073.01"},{"v":107.99703558247566,"d":"108.00"},{"v":2.771429046061224,"d":"2.77"},{"v":4316.61711752646,"d":"4316.62"}]
[24,{"v":152.0814971211069,"d":"152.08"},null,{"v":2183.879767763291,"d":"2183.88"},{"v":0,"d":"0.00"},null,{"v":2180.0288395690936,"d":"2180.03"},{"v":166.64181479532778,"d":"166.64"},{"v":2.771429046061224,"d":"2.77"},{"v":4685.403348294881,"d":"4685.40"}]
[25,{"v":137.1569265128446,"d":"137.16"},null,{"v":2316.263207104338,"d":"2316.26"},{"v":0,"d":"0.00"},null,{"v":2335.761909899125,"d":"2335.76"},{"v":143.5986933159253,"d":"143.60"},{"v":2.771429046061224,"d":"2.77"},{"v":4935.5521658782945,"d":"4935.55"}]
[26,{"v":112.1231389164417,"d":"112.12"},null,{"v":2423.208643128192,"d":"2423.21"},{"v":0,"d":"0.00"},null,{"v":2476.6857114667287,"d":"2476.69"},{"v":153.49853110191086,"d":"153.50"},{"v":2.771429046061224,"d":"2.77"},{"v":5168.2874536593345,"d":"5168.29"}]
[27,{"v":61.421670250801945,"d":"61.42"},null,{"v":2535.035137887445,"d":"2535.04"},{"v":0,"d":"0.00"},null,{"v":2590.1621946130313,"d":"2590.16"},{"v":93.48555247309817,"d":"93.49"},{"v":2.771429046061224,"d":"2.77"},{"v":5282.884845748546,"d":"5282.88"}]
[28,{"v":56.21323000276435,"d":"56.21"},661.81,{"v":660.806641325041,"d":"660.81"},{"v":1985.6371425165005,"d":"1985.64"},null,{"v":1355.2117812648712,"d":"1355.21"},{"v":40.220441795326046,"d":"40.22"},{"v":2.7802905241683673,"d":"2.78"},{"v":4762.679527428672,"d":"4762.68"}]
[29,{"v":4.579981001783724,"d":"4.58"},661.81,{"v":661.0177388068688,"d":"661.02"},{"v":0,"d":"0.00"},null,{"v":1412.0086346784003,"d":"1412.01"},{"v":3.463151798426948,"d":"3.46"},{"v":2.7802905241683673,"d":"2.78"},{"v":2742.8795062854797,"d":"2742.88"}]

{"sheet":"下管段轴向合力","index":14,"n_rows":33,"n_cols":10,"rows_kept":33,"merged":[[0,0,0,9]],"flags":["formulas_cached_only"]}
["下游管段轴向力合力计算"]
["编号","A1'","A2'","A3'","A4'","A5'","A6'","A7'","A8'","∑A'"]
[0,{"v":2.7318970454484424,"d":"2.73"},null,{"v":-18.415376191911147,"d":"-18.42"},{"v":0,"d":"0.00"},null,{"v":-28.69757284959277,"d":"-28.70"},{"v":-39.65073123160587,"d":"-39.65"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-86.80321227372258,"d":"-86.80"}]
[1,{"v":4.403218578207072,"d":"4.40"},null,{"v":-45.68003494966369,"d":"-45.68"},{"v":0,"d":"0.00"},null,{"v":-63.30481414689391,"d":"-63.30"},{"v":-41.50174599456712,"d":"-41.50"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-148.85480555897888,"d":"-148.85"}]
["1'",{"v":0.3520801984539817,"d":"0.35"},null,{"v":-84.07199922737425,"d":"-84.07"},{"v":0,"d":"0.00"},null,{"v":-90.70207975078714,"d":"-90.70"},{"v":-2.1526132536852725,"d":"-2.15"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-179.3460410794539,"d":"-179.35"}]
[2,{"v":0.5106122894699447,"d":"0.51"},null,{"v":-138.9554615674053,"d":"-138.96"},{"v":0,"d":"0.00"},null,{"v":-149.36054913886795,"d":"-149.36"},{"v":-2.3206737684637746,"d":"-2.32"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-292.8975012313283,"d":"-292.90"}]
[3,{"v":3.1825515935948903,"d":"3.18"},null,{"v":-203.66477447845656,"d":"-203.66"},{"v":0,"d":"0.00"},null,{"v":-225.3383079706022,"d":"-225.34"},{"v":-41.61630420980469,"d":"-41.62"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-470.20826411132975,"d":"-470.21"}]
[4,{"v":3.4577099360283774,"d":"3.46"},null,{"v":-228.35761974027287,"d":"-228.36"},{"v":0,"d":"0.00"},null,{"v":-252.3879825068364,"d":"-252.39"},{"v":-45.21438359605052,"d":"-45.21"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-525.2737049531927,"d":"-525.27"}]
[5,{"v":0.4848315929155186,"d":"0.48"},null,{"v":-255.38765656202492,"d":"-255.39"},{"v":0,"d":"0.00"},null,{"v":-273.64558348284817,"d":"-273.65"},{"v":-2.3261779351146155,"d":"-2.33"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-533.6460154331335,"d":"-533.65"}]
[6,{"v":6.733936352393468,"d":"6.73"},null,{"v":-317.24723435506473,"d":"-317.25"},{"v":0,"d":"0.00"},null,{"v":-355.41247806826857,"d":"-355.41"},{"v":-64.66718272850157,"d":"-64.67"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-733.3643878455026,"d":"-733.36"}]
[7,{"v":6.734613105183465,"d":"6.73"},null,{"v":-364.08723371852443,"d":"-364.09"},{"v":0,"d":"0.00"},null,{"v":-405.427808085453,"d":"-405.43"},{"v":-64.67368170533216,"d":"-64.67"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-830.2255394501873,"d":"-830.23"}]
[8,{"v":5.328197761607948,"d":"5.33"},null,{"v":-408.1620608675826,"d":"-408.16"},{"v":0,"d":"0.00"},null,{"v":-448.99401540857633,"d":"-448.99"},{"v":-51.16762621925083,"d":"-51.17"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-905.766933779863,"d":"-905.77"}]
[9,{"v":0.7078003044153048,"d":"0.71"},null,{"v":-448.2552884404776,"d":"-448.26"},{"v":0,"d":"0.00"},null,{"v":-479.6881287281447,"d":"-479.69"},{"v":-2.4828559988157264,"d":"-2.48"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-932.489901909084,"d":"-932.49"}]
[10,{"v":1.6199826956092245,"d":"1.62"},null,{"v":-534.8970801633735,"d":"-534.90"},{"v":0,"d":"0.00"},null,{"v":-572.2718312132132,"d":"-572.27"},{"v":-2.1453339299715855,"d":"-2.15"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-1110.4656916570104,"d":"-1110.47"}]
[11,{"v":2.0652168201391095,"d":"2.07"},null,{"v":-684.1406879588787,"d":"-684.14"},{"v":0,"d":"0.00"},null,{"v":-731.4969702706161,"d":"-731.50"},{"v":-2.234851222991869,"d":"-2.23"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-1418.5787216784088,"d":"-1418.58"}]
[12,{"v":2.510939157096299,"d":"2.51"},null,{"v":-846.4401500669771,"d":"-846.44"},{"v":0,"d":"0.00"},null,{"v":-904.6740824806703,"d":"-904.67"},{"v":-2.3312608072740333,"d":"-2.33"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-1753.7059832438865,"d":"-1753.71"}]
[13,{"v":2.4119381229338135,"d":"2.41"},null,{"v":-964.3840331733625,"d":"-964.38"},{"v":0,"d":"0.00"},null,{"v":-1030.7275871348363,"d":"-1030.73"},{"v":-2.3815874270863127,"d":"-2.38"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-1997.8526986584125,"d":"-1997.85"}]
[14,{"v":2.2158029757429305,"d":"2.22"},null,{"v":-1113.2033902786643,"d":"-1113.20"},{"v":0,"d":"0.00"},null,{"v":-1189.9380144320573,"d":"-1189.94"},{"v":-2.7517061803403244,"d":"-2.75"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-2306.4487369613807,"d":"-2306.45"}]
[15,{"v":1.0493435632292218,"d":"1.05"},null,{"v":-1238.8878939678973,"d":"-1238.89"},{"v":0,"d":"0.00"},null,{"v":-1323.8321447427734,"d":"-1323.83"},{"v":-3.026967538026804,"d":"-3.03"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-2567.4690917315297,"d":"-2567.47"}]
[16,{"v":2.642348024786623,"d":"2.64"},null,{"v":-1302.3824636303627,"d":"-1302.38"},{"v":0,"d":"0.00"},null,{"v":-1391.8957326373074,"d":"-1391.90"},{"v":-2.862239535664378,"d":"-2.86"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-2697.269516824609,"d":"-2697.27"}]
[17,{"v":3.1105130787917474,"d":"3.11"},null,{"v":-1445.8816442715417,"d":"-1445.88"},{"v":0,"d":"0.00"},null,{"v":-1544.8536171137912,"d":"-1544.85"},{"v":-2.6828214629483895,"d":"-2.68"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-2993.078998815551,"d":"-2993.08"}]
[18,{"v":0.8873715537840765,"d":"0.89"},null,{"v":-1667.079322172231,"d":"-1667.08"},{"v":0,"d":"0.00"},null,{"v":-1780.8424216753149,"d":"-1780.84"},{"v":-3.2373836436358494,"d":"-3.24"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-3453.043184983459,"d":"-3453.04"}]
[19,{"v":0.5738773750634906,"d":"0.57"},null,{"v":-1725.9976946698305,"d":"-1726.00"},{"v":0,"d":"0.00"},null,{"v":-1843.4526494942222,"d":"-1843.45"},{"v":-3.4522062826670297,"d":"-3.45"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-3575.1001021177176,"d":"-3575.10"}]
[20,{"v":1.3864583159409385,"d":"1.39"},null,{"v":-1766.5776732199224,"d":"-1766.58"},{"v":0,"d":"0.00"},null,{"v":-1887.3120571189907,"d":"-1887.31"},{"v":-3.374771914699241,"d":"-3.37"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-3658.6494729837323,"d":"-3658.65"}]
[21,{"v":2.4962214175628743,"d":"2.50"},null,{"v":-1855.2505126824442,"d":"-1855.25"},{"v":0,"d":"0.00"},null,{"v":-1982.2880880063283,"d":"-1982.29"},{"v":-3.1558065666199075,"d":"-3.16"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-3840.969614883891,"d":"-3840.97"}]
[22,{"v":2.8805970812495056,"d":"2.88"},null,{"v":-1940.2246441799396,"d":"-1940.22"},{"v":0,"d":"0.00"},null,{"v":-2073.0145222106826,"d":"-2073.01"},{"v":-3.2845314269088264,"d":"-3.28"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-4016.414529782343,"d":"-4016.41"}]
[23,{"v":3.1503810979224203,"d":"3.15"},null,{"v":-2040.4482976692768,"d":"-2040.45"},{"v":0,"d":"0.00"},null,{"v":-2180.0288395690936,"d":"-2180.03"},{"v":-3.451999312162402,"d":"-3.45"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-4223.550184498671,"d":"-4223.55"}]
[24,{"v":3.2677807257810376,"d":"3.27"},null,{"v":-2186.3091006230165,"d":"-2186.31"},{"v":0,"d":"0.00"},null,{"v":-2335.761909899125,"d":"-2335.76"},{"v":-3.4212566160206155,"d":"-3.42"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-4524.995915458441,"d":"-4525.00"}]
[25,{"v":2.6119490976877424,"d":"2.61"},null,{"v":-2318.3006837208145,"d":"-2318.30"},{"v":0,"d":"0.00"},null,{"v":-2476.6857114667287,"d":"-2476.69"},{"v":-3.5758038321315455,"d":"-3.58"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-4798.721678968049,"d":"-4798.72"}]
[26,{"v":2.3791172580393516,"d":"2.38"},null,{"v":-2424.614887128667,"d":"-2424.61"},{"v":0,"d":"0.00"},null,{"v":-2590.1621946130313,"d":"-2590.16"},{"v":-3.621085039822526,"d":"-3.62"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-5018.790478569542,"d":"-5018.79"}]
[27,{"v":3.612098306417666,"d":"3.61"},null,{"v":-2537.2592499349757,"d":"-2537.26"},{"v":0,"d":"0.00"},null,{"v":-2710.4235625297424,"d":"-2710.42"},{"v":-3.3227537525447746,"d":"-3.32"},{"v":-2.771429046061224,"d":"-2.77"},{"v":-5250.164896956906,"d":"-5250.16"}]
[28,{"v":0,"d":"0.00"},null,{"v":-661.2043491900001,"d":"-661.20"},{"v":0,"d":"0.00"},null,{"v":-1412.0086346784003,"d":"-1412.01"},{"v":-1.524,"d":"-1.52"},{"v":-2.7802905241683673,"d":"-2.78"},{"v":-2077.5172743925687,"d":"-2077.52"}]
[29,{"v":0,"d":"0.00"},null,{"v":-661.4154466718279,"d":"-661.42"},{"v":0,"d":"0.00"},null,{"v":-1412.4594355048994,"d":"-1412.46"},{"v":-1.3319999999999999,"d":"-1.33"},{"v":-2.7802905241683673,"d":"-2.78"},{"v":-2077.9871727008954,"d":"-2077.99"}]

{"sheet":"上下管段法向合力","index":15,"n_rows":33,"n_cols":9,"rows_kept":33,"merged":[[0,0,0,3],[0,5,0,8]],"flags":["formulas_cached_only"]}
["上管段法向合力",{"$nulls":4},"下管段法向合力"]
["编号","Qs","Qw","Q",null,"编号","Qs'","Qw'","Q'"]
[0,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,0,{"v":4.434010484988287,"d":"4.43"},{"v":13.80023488024444,"d":"13.80"},{"v":18.234245365232727,"d":"18.23"}]
[1,{"v":4.434010484988287,"d":"4.43"},{"v":13.80023488024444,"d":"13.80"},{"v":18.234245365232727,"d":"18.23"},null,1,{"v":4.412362113979623,"d":"4.41"},{"v":13.732857365981522,"d":"13.73"},{"v":18.145219479961145,"d":"18.15"}]
["1'",{"v":4.412362113979623,"d":"4.41"},{"v":13.732857365981522,"d":"13.73"},{"v":18.145219479961145,"d":"18.15"},null,"1'",{"v":4.362080591484273,"d":"4.36"},{"v":13.576363189226331,"d":"13.58"},{"v":17.938443780710603,"d":"17.94"}]
[2,{"v":4.362080591484273,"d":"4.36"},{"v":13.576363189226331,"d":"13.58"},{"v":17.938443780710603,"d":"17.94"},null,2,{"v":5.811451566649604,"d":"5.81"},{"v":13.527496503881851,"d":"13.53"},{"v":19.338948070531455,"d":"19.34"}]
[3,{"v":5.811451566649604,"d":"5.81"},{"v":13.527496503881851,"d":"13.53"},{"v":19.338948070531455,"d":"19.34"},null,3,{"v":5.9327354056789305,"d":"5.93"},{"v":13.809812667000537,"d":"13.81"},{"v":19.74254807267947,"d":"19.74"}]
[4,{"v":5.9327354056789305,"d":"5.93"},{"v":13.809812667000537,"d":"13.81"},{"v":19.74254807267947,"d":"19.74"},null,4,{"v":5.9327354056789305,"d":"5.93"},{"v":13.809812667000537,"d":"13.81"},{"v":19.74254807267947,"d":"19.74"}]
[5,{"v":5.9327354056789305,"d":"5.93"},{"v":13.809812667000537,"d":"13.81"},{"v":19.74254807267947,"d":"19.74"},null,5,{"v":5.825235148961263,"d":"5.83"},{"v":13.559580976993866,"d":"13.56"},{"v":19.38481612595513,"d":"19.38"}]
[6,{"v":5.825235148961263,"d":"5.83"},{"v":13.559580976993866,"d":"13.56"},{"v":19.38481612595513,"d":"19.38"},null,6,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"}]
[7,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"},null,7,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"}]
[8,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"},null,8,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"}]
[9,{"v":5.918107153643751,"d":"5.92"},{"v":13.775762029910245,"d":"13.78"},{"v":19.693869183553996,"d":"19.69"},null,9,{"v":7.236806412823616,"d":"7.24"},{"v":13.453660243974104,"d":"13.45"},{"v":20.69046665679772,"d":"20.69"}]
[10,{"v":7.236806412823616,"d":"7.24"},{"v":13.453660243974104,"d":"13.45"},{"v":20.69046665679772,"d":"20.69"},null,10,{"v":6.253027299799809,"d":"6.25"},{"v":11.624755449963404,"d":"11.62"},{"v":17.877782749763213,"d":"17.88"}]
[11,{"v":6.253027299799809,"d":"6.25"},{"v":11.624755449963404,"d":"11.62"},{"v":17.877782749763213,"d":"17.88"},null,11,{"v":7.3106427067899205,"d":"7.31"},{"v":11.313117484808984,"d":"11.31"},{"v":18.623760191598905,"d":"18.62"}]
[12,{"v":7.3106427067899205,"d":"7.31"},{"v":11.313117484808984,"d":"11.31"},{"v":18.623760191598905,"d":"18.62"},null,12,{"v":8.354484031554748,"d":"8.35"},{"v":11.07268936239553,"d":"11.07"},{"v":19.427173393950277,"d":"19.43"}]
[13,{"v":8.35448403155475,"d":"8.35"},{"v":11.07268936239553,"d":"11.07"},{"v":19.427173393950277,"d":"19.43"},null,13,{"v":8.534838344668028,"d":"8.53"},{"v":11.311723547717914,"d":"11.31"},{"v":19.846561892385942,"d":"19.85"}]
[14,{"v":9.800771304881948,"d":"9.80"},{"v":11.311723547717914,"d":"11.31"},{"v":21.112494852599863,"d":"21.11"},null,14,{"v":10.644898183134718,"d":"10.64"},{"v":12.285986653034653,"d":"12.29"},{"v":22.93088483616937,"d":"22.93"}]
[15,{"v":10.644898183134718,"d":"10.64"},{"v":12.285986653034653,"d":"12.29"},{"v":22.93088483616937,"d":"22.93"},null,15,{"v":11.709739025248759,"d":"11.71"},{"v":13.514990458307942,"d":"13.51"},{"v":25.2247294835567,"d":"25.22"}]
[16,{"v":11.709739025248759,"d":"11.71"},{"v":13.514990458307942,"d":"13.51"},{"v":25.2247294835567,"d":"25.22"},null,16,{"v":11.773380174122211,"d":"11.77"},{"v":12.078615956414268,"d":"12.08"},{"v":23.851996130536477,"d":"23.85"}]
[17,{"v":11.773380174122211,"d":"11.77"},{"v":12.078615956414268,"d":"12.08"},{"v":23.851996130536477,"d":"23.85"},null,17,{"v":11.035371648325182,"d":"11.04"},{"v":11.321473876244724,"d":"11.32"},{"v":22.356845524569906,"d":"22.36"}]
[18,{"v":11.035371648325183,"d":"11.04"},{"v":11.321473876244724,"d":"11.32"},{"v":22.356845524569906,"d":"22.36"},null,18,{"v":13.31647751038512,"d":"13.32"},{"v":13.661719519913623,"d":"13.66"},{"v":26.978197030298745,"d":"26.98"}]
[19,{"v":13.31647751038512,"d":"13.32"},{"v":13.661719519913623,"d":"13.66"},{"v":26.978197030298745,"d":"26.98"},null,19,{"v":14.981460367398732,"d":"14.98"},{"v":13.786925321493186,"d":"13.79"},{"v":28.768385688891918,"d":"28.77"}]
[20,{"v":14.981460367398732,"d":"14.98"},{"v":13.786925321493186,"d":"13.79"},{"v":28.768385688891918,"d":"28.77"},null,20,{"v":14.64542021805755,"d":"14.65"},{"v":13.477679071102795,"d":"13.48"},{"v":28.123099289160344,"d":"28.12"}]
[21,{"v":14.64542021805755,"d":"14.65"},{"v":13.477679071102795,"d":"13.48"},{"v":28.123099289160344,"d":"28.12"},null,21,{"v":13.69518132284591,"d":"13.70"},{"v":12.60320673231999,"d":"12.60"},{"v":26.2983880551659,"d":"26.30"}]
[22,{"v":13.69518132284591,"d":"13.70"},{"v":12.60320673231999,"d":"12.60"},{"v":26.2983880551659,"d":"26.30"},null,22,{"v":14.901040327670254,"d":"14.90"},{"v":12.47005489656997,"d":"12.47"},{"v":27.37109522424022,"d":"27.37"}]
[23,{"v":14.901040327670254,"d":"14.90"},{"v":12.47005489656997,"d":"12.47"},{"v":27.37109522424022,"d":"27.37"},null,23,{"v":16.296606038116714,"d":"16.30"},{"v":12.47005489656997,"d":"12.47"},{"v":28.766660934686684,"d":"28.77"}]
[24,{"v":16.296606038116714,"d":"16.30"},{"v":12.47005489656997,"d":"12.47"},{"v":28.766660934686684,"d":"28.77"},null,24,{"v":16.15147228742127,"d":"16.15"},{"v":12.358999512750527,"d":"12.36"},{"v":28.5104718001718,"d":"28.51"}]
[25,{"v":16.15147228742127,"d":"16.15"},{"v":12.358999512750527,"d":"12.36"},{"v":28.5104718001718,"d":"28.51"},null,25,{"v":16.881077037449394,"d":"16.88"},{"v":12.917288230313485,"d":"12.92"},{"v":29.79836526776288,"d":"29.80"}]
[26,{"v":16.881077037449394,"d":"16.88"},{"v":12.917288230313485,"d":"12.92"},{"v":29.79836526776288,"d":"29.80"},null,26,{"v":17.094845910481933,"d":"17.09"},{"v":13.080862754705786,"d":"13.08"},{"v":30.17570866518772,"d":"30.18"}]
[27,{"v":17.094845910481933,"d":"17.09"},{"v":13.080862754705786,"d":"13.08"},{"v":30.17570866518772,"d":"30.18"},null,27,{"v":15.68644833621816,"d":"15.69"},{"v":5.97991676905554,"d":"5.98"},{"v":21.666365105273698,"d":"21.67"}]
[28,{"v":8.016555088951268,"d":"8.02"},{"v":2.98995838452777,"d":"2.99"},{"v":11.006513473479039,"d":"11.01"},null,28,1.85,1.38,3.23]
[29,{"v":2.651963088885501,"d":"2.65"},{"v":1.1959833538111082,"d":"1.20"},{"v":3.8479464426966095,"d":"3.85"},null,29,1.53,1.38,2.91]

{"sheet":"镇墩上下游面作用的弯矩","index":16,"n_rows":33,"n_cols":9,"rows_kept":33,"merged":[[0,0,0,8]],"flags":["formulas_cached_only"]}
["镇墩上下游面作用的弯矩"]
["编号","q上","q下","l1","l2","a1","a2","M上","M下"]
[0,3.66,3.66,{"v":0,"d":"0.00"},{"v":10,"d":"10.00"},{"v":0,"d":"0.00"},{"v":4.861,"d":"4.86"},{"v":0,"d":"0.00"},{"v":33.15317339133223,"d":"33.15"}]
[1,3.66,3.66,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":4.861,"d":"4.86"},{"v":7.461,"d":"7.46"},{"v":33.15317339133223,"d":"33.15"},{"v":32.9913081453839,"d":"32.99"}]
["1'",3.66,3.66,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":7.461,"d":"7.46"},{"v":11.414,"d":"11.41"},{"v":32.9913081453839,"d":"32.99"},{"v":32.61535232856474,"d":"32.62"}]
[2,3.66,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":11.414,"d":"11.41"},{"v":12.395,"d":"12.40"},{"v":32.61535232856474,"d":"32.62"},{"v":35.16172376460265,"d":"35.16"}]
[3,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":12.395,"d":"12.40"},{"v":4.368,"d":"4.37"},{"v":35.16172376460265,"d":"35.16"},{"v":35.895541950326304,"d":"35.90"}]
[4,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":4.368,"d":"4.37"},{"v":35.895541950326304,"d":"35.90"},{"v":35.895541950326304,"d":"35.90"}]
[5,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":4.368,"d":"4.37"},{"v":11.760000000000002,"d":"11.76"},{"v":35.895541950326304,"d":"35.90"},{"v":35.24512022900932,"d":"35.25"}]
[6,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":11.760000000000002,"d":"11.76"},{"v":5.9380000000000015,"d":"5.94"},{"v":35.24512022900932,"d":"35.25"},{"v":35.80703487918908,"d":"35.81"}]
[7,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},{"v":35.80703487918908,"d":"35.81"},{"v":35.80703487918908,"d":"35.81"}]
[8,3.96,3.96,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":5.9380000000000015,"d":"5.94"},{"v":35.80703487918908,"d":"35.81"},{"v":35.80703487918908,"d":"35.81"}]
[9,3.96,4.26,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":5.9380000000000015,"d":"5.94"},{"v":13.747000000000002,"d":"13.75"},{"v":35.80703487918908,"d":"35.81"},{"v":37.619030285086765,"d":"37.62"}]
[10,4.26,4.26,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":13.747000000000002,"d":"13.75"},{"v":32.947,"d":"32.95"},{"v":37.619030285086765,"d":"37.62"},{"v":32.505059545024025,"d":"32.51"}]
[11,4.26,{"v":4.5600000000000005,"d":"4.56"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":32.947,"d":"32.95"},{"v":35.249,"d":"35.25"},{"v":32.505059545024025,"d":"32.51"},{"v":33.86138216654347,"d":"33.86"}]
[12,{"v":4.5600000000000005,"d":"4.56"},{"v":4.859999999999999,"d":"4.86"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":35.249,"d":"35.25"},{"v":36.939,"d":"36.94"},{"v":33.86138216654347,"d":"33.86"},{"v":35.32213344354596,"d":"35.32"}]
[13,{"v":4.859999999999999,"d":"4.86"},{"v":4.859999999999999,"d":"4.86"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":36.939,"d":"36.94"},{"v":35.259,"d":"35.26"},{"v":35.32213344354596,"d":"35.32"},{"v":36.08465798615626,"d":"36.08"}]
[14,5.17,5.17,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":35.259,"d":"35.26"},{"v":27.506,"d":"27.51"},{"v":38.386354277454295,"d":"38.39"},{"v":41.69251788394431,"d":"41.69"}]
[15,5.17,5.17,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":27.506,"d":"27.51"},{"v":12.634,"d":"12.63"},{"v":41.69251788394431,"d":"41.69"},{"v":45.863144515557636,"d":"45.86"}]
[16,5.17,{"v":5.470000000000001,"d":"5.47"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":12.634,"d":"12.63"},{"v":29.311,"d":"29.31"},{"v":45.863144515557636,"d":"45.86"},{"v":43.36726569188452,"d":"43.37"}]
[17,{"v":5.470000000000001,"d":"5.47"},{"v":5.470000000000001,"d":"5.47"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":29.311,"d":"29.31"},{"v":35.189,"d":"35.19"},{"v":43.36726569188452,"d":"43.37"},{"v":40.64881004467257,"d":"40.65"}]
[18,{"v":5.470000000000001,"d":"5.47"},{"v":5.470000000000001,"d":"5.47"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":35.189,"d":"35.19"},{"v":9.463000000000001,"d":"9.46"},{"v":40.64881004467257,"d":"40.65"},{"v":49.05126732781591,"d":"49.05"}]
[19,{"v":5.470000000000001,"d":"5.47"},{"v":5.779999999999999,"d":"5.78"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":9.463000000000001,"d":"9.46"},{"v":5.473000000000001,"d":"5.47"},{"v":49.05126732781591,"d":"49.05"},{"v":52.3061557979853,"d":"52.31"}]
[20,{"v":5.779999999999999,"d":"5.78"},{"v":5.779999999999999,"d":"5.78"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":5.473000000000001,"d":"5.47"},{"v":13.322000000000001,"d":"13.32"},{"v":52.3061557979853,"d":"52.31"},{"v":51.13290779847335,"d":"51.13"}]
[21,{"v":5.779999999999999,"d":"5.78"},{"v":5.779999999999999,"d":"5.78"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":13.322000000000001,"d":"13.32"},24.51,{"v":51.13290779847335,"d":"51.13"},{"v":47.81525100939254,"d":"47.82"}]
[22,{"v":5.779999999999999,"d":"5.78"},6.08,{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},24.51,{"v":25.807000000000002,"d":"25.81"},{"v":47.81525100939254,"d":"47.82"},{"v":49.76562768043677,"d":"49.77"}]
[23,6.08,{"v":6.390000000000001,"d":"6.39"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":25.807000000000002,"d":"25.81"},{"v":49.76562768043677,"d":"49.77"},{"v":52.30301988124852,"d":"52.30"}]
[24,{"v":6.390000000000001,"d":"6.39"},{"v":6.390000000000001,"d":"6.39"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":25.807000000000002,"d":"25.81"},{"v":26.844,"d":"26.84"},{"v":52.30301988124852,"d":"52.30"},{"v":51.83722145485781,"d":"51.84"}]
[25,{"v":6.390000000000001,"d":"6.39"},{"v":6.390000000000001,"d":"6.39"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":26.844,"d":"26.84"},{"v":21.158,"d":"21.16"},{"v":51.83722145485781,"d":"51.84"},{"v":54.178845941387046,"d":"54.18"}]
[26,{"v":6.390000000000001,"d":"6.39"},{"v":6.390000000000001,"d":"6.39"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":21.158,"d":"21.16"},{"v":19.194000000000003,"d":"19.19"},{"v":54.178845941387046,"d":"54.18"},{"v":54.86492484579585,"d":"54.86"}]
[27,{"v":6.390000000000001,"d":"6.39"},{"v":5,"d":"5.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":19.194000000000003,"d":"19.19"},{"v":29.943000000000005,"d":"29.94"},{"v":54.86492484579585,"d":"54.86"},{"v":39.39339110049763,"d":"39.39"}]
[28,2.54,3.23,{"v":10,"d":"10.00"},{"v":2,"d":"2.00"},{"v":29.943000000000005,"d":"29.94"},{"v":0,"d":"0.00"},{"v":20.011842679052798,"d":"20.01"},{"v":1.1745454545454546,"d":"1.17"}]
[29,{"v":2.2199999999999998,"d":"2.22"},2.91,{"v":4,"d":"4.00"},{"v":2,"d":"2.00"},{"v":29.943,"d":"29.94"},{"v":0,"d":"0.00"},{"v":2.798506503779352,"d":"2.80"},{"v":1.0581818181818183,"d":"1.06"}]

{"sheet":"体积计算","index":17,"n_rows":35,"n_cols":15,"rows_kept":35,"merged":[[0,0,0,13]],"flags":["formulas_cached_only"]}
["体 积 计 算"]
["编号","∑A","a1","β","∑A'","a2","f","K","∑X","∑Y","∑Z","∑P","G","V","V'"]
[0,21.146928846061204,0,11.23,{"v":-86.80321227372258,"d":"-86.80"},4.861,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-63.69003824478055,"d":"-63.69"},{"v":-7.3518724363506704,"d":"-7.35"},{"v":-16.83557684025127,"d":"-16.84"},{"v":65.87759573000228,"d":"65.88"},{"v":336.73985108636214,"d":"336.74"},{"v":15.306356867561915,"d":"15.31"},{"v":15.306356867561915,"d":"15.31"}]
[1,119.39769259550911,4.861,{"v":26.957,"d":"26.96"},{"v":-148.85480555897888,"d":"-148.85"},7.461,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-12.606347102668494,"d":"-12.61"},{"v":-9.206757602612312,"d":"-9.21"},{"v":-66.87699426783182,"d":"-66.88"},{"v":68.0547746272998,"d":"68.05"},{"v":349.48063073911135,"d":"349.48"},{"v":15.885483215414153,"d":"15.89"},{"v":15.885483215414153,"d":"15.89"}]
["1'",195.7380368166115,7.461,{"v":4.698,"d":"4.70"},{"v":-179.3460410794539,"d":"-179.35"},11.414,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":18.869878407302906,"d":"18.87"},{"v":-10.070236396596176,"d":"-10.07"},{"v":-14.39160934125166,"d":"-14.39"},{"v":23.73163986195641,"d":"23.73"},{"v":128.72843570637824,"d":"128.73"},{"v":5.8512925321081015,"d":"5.85"},{"v":5.8512925321081015,"d":"5.85"}]
[2,278.5711095056774,11.414,{"v":55.788,"d":"55.79"},{"v":-292.8975012313283,"d":"-292.90"},12.395,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":112.10175557674245,"d":"112.10"},{"v":-7.738331872230603,"d":"-7.74"},{"v":-236.4958275495544,"d":"-236.50"},{"v":261.7194682321823,"d":"261.72"},{"v":1316.3356730331423,"d":"1316.34"},{"v":59.83343968332465,"d":"59.83"},{"v":13.942037837523122,"d":"13.94"}]
[3,414.08001005950604,12.395,{"v":43.734,"d":"43.73"},{"v":-470.20826411132975,"d":"-470.21"},4.368,{"v":0.5,"d":"0.50"},{"v":1.5,"d":"1.50"},{"v":65.54611237123072,"d":"65.55"},{"v":53.04400326470565,"d":"53.04"},{"v":-323.98597658995476,"d":"-323.99"},{"v":330.5498538404286,"d":"330.55"},{"v":938.6055582565803,"d":"938.61"},{"v":42.66388901166274,"d":"42.66"},{"v":4.335428856445933,"d":"4.34"}]
[4,501.20183135788517,4.368,{"v":0,"d":"0.00"},{"v":-525.2737049531927,"d":"-525.27"},4.368,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-24.002026346203195,"d":"-24.00"},{"v":-1.8324381748461462,"d":"-1.83"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-118.17769355616983,"d":"-118.18"},{"v":-5.371713343462265,"d":"-5.37"},{"v":-5.371713343462265,"d":"-5.37"}]
[5,558.9521918325744,4.368,{"v":0,"d":"0.00"},{"v":-533.6460154331335,"d":"-533.65"},{"v":11.760000000000002,"d":"11.760"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":34.874274346679385,"d":"34.87"},{"v":-66.15996717879383,"d":"-66.16"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":240.53133891219076,"d":"240.53"},{"v":10.933242677826852,"d":"10.93"},{"v":10.933242677826852,"d":"10.93"}]
[6,712.2629819384306,11.760000000000002,{"v":0,"d":"0.00"},{"v":-733.3643878455026,"d":"-733.36"},{"v":5.9380000000000015,"d":"5.938"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-32.10582726795508,"d":"-32.11"},{"v":69.2657744443156,"d":"69.27"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-229.79491078409097,"d":"-229.79"},{"v":-10.44522321745868,"d":"-10.45"},{"v":-10.44522321745868,"d":"-10.45"}]
[7,793.5531814634685,5.9380000000000015,{"v":0,"d":"0.00"},{"v":-830.2255394501873,"d":"-830.23"},{"v":5.9380000000000015,"d":"5.938"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-36.47578893145965,"d":"-36.48"},{"v":-3.7919206391565297,"d":"-3.79"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-178.5870240181417,"d":"-178.59"},{"v":-8.117592000824622,"d":"-8.12"},{"v":-8.117592000824622,"d":"-8.12"}]
[8,887.6505143593319,5.9380000000000015,{"v":0,"d":"0.00"},{"v":-905.766933779863,"d":"-905.77"},{"v":5.9380000000000015,"d":"5.938"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-18.019312835471624,"d":"-18.02"},{"v":-1.8732371867990452,"d":"-1.87"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-88.22332699055907,"d":"-88.22"},{"v":-4.010151226843594,"d":"-4.01"},{"v":-4.010151226843594,"d":"-4.01"}]
[9,956.1353358373882,5.9380000000000015,{"v":0,"d":"0.00"},{"v":-932.489901909084,"d":"-932.49"},{"v":13.747000000000002,"d":"13.747"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":45.20509268322155,"d":"45.21"},{"v":-122.61772971656904,"d":"-122.62"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":348.6431931326768,"d":"348.64"},{"v":15.847417869667128,"d":"15.85"},{"v":15.847417869667128,"d":"15.85"}]
[10,1177.8066176772636,13.747000000000002,34.87,{"v":-1110.4656916570104,"d":"-1110.47"},32.947,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":379.23579296320486,"d":"379.24"},{"v":-323.92057785830804,"d":"-323.92"},{"v":-532.6322604954926,"d":"-532.63"},{"v":653.8477740154577,"d":"653.85"},{"v":3593.159447935597,"d":"3593.16"},{"v":163.32542945161805,"d":"163.33"},{"v":54.47051343618313,"d":"54.47"}]
[11,1396.1519994113157,32.947,{"v":2.246,"d":"2.25"},{"v":-1418.5787216784088,"d":"-1418.58"},35.249,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":13.985142940566448,"d":"13.99"},{"v":-59.370459751150065,"d":"-59.37"},{"v":-45.38807259142552,"d":"-45.39"},{"v":47.49380334983279,"d":"47.49"},{"v":296.83947650031405,"d":"296.84"},{"v":13.492703477287002,"d":"13.49"},{"v":13.492703477287002,"d":"13.49"}]
[12,1737.793550185414,35.249,{"v":0,"d":"0.00"},{"v":-1753.7059832438865,"d":"-1753.71"},36.939,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":17.44556044454248,"d":"17.45"},{"v":-50.96495282037347,"d":"-50.96"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":138.19275504308587,"d":"138.19"},{"v":6.281488865594812,"d":"6.28"},{"v":6.281488865594812,"d":"6.28"}]
[13,1990.9858096581415,36.939,{"v":0,"d":"0.00"},{"v":-1997.8526986584125,"d":"-1997.85"},35.259,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-39.97039862844713,"d":"-39.97"},{"v":43.19309636202934,"d":"43.19"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-243.04508950426498,"d":"-243.05"},{"v":-11.04750406837568,"d":"-11.05"},{"v":-11.04750406837568,"d":"-11.05"}]
[14,2327.081409102246,35.259,{"v":0,"d":"0.00"},{"v":-2306.4487369613807,"d":"-2306.45"},27.506,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-145.3932725933355,"d":"-145.39"},{"v":278.0536374241335,"d":"278.05"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-1005.020000390811,"d":"-1005.02"},{"v":-45.68272729049141,"d":"-45.68"},{"v":-45.68272729049141,"d":"-45.68"}]
[15,2759.872838818559,27.506,{"v":0,"d":"0.00"},{"v":-2567.4690917315297,"d":"-2567.47"},12.634,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-57.15230432884482,"d":"-57.15"},{"v":712.7452674432907,"d":"712.75"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-998.5067890875148,"d":"-998.51"},{"v":-45.38667223125067,"d":"-45.39"},{"v":-45.38667223125067,"d":"-45.39"}]
[16,2690.0955813229502,12.634,{"v":0,"d":"0.00"},{"v":-2697.269516824609,"d":"-2697.27"},29.311,{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":272.73165984465686,"d":"272.73"},{"v":-731.747405004535,"d":"-731.75"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2277.226810790924,"d":"2277.23"},{"v":103.51030958140564,"d":"103.51"},{"v":52.58773228079392,"d":"52.59"}]
[17,3063.1311783089513,29.311,{"v":0,"d":"0.00"},{"v":-2993.078998815551,"d":"-2993.08"},35.189,{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":224.71620449715283,"d":"224.72"},{"v":-225.21347277883365,"d":"-225.21"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1498.6052982626998,"d":"1498.61"},{"v":68.11842264830453,"d":"68.12"},{"v":34.6071167993348,"d":"34.61"}]
[18,3515.5826149787054,35.189,{"v":0,"d":"0.00"},{"v":-3453.043184983459,"d":"-3453.04"},{"v":9.463000000000001,"d":"9.463"},{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-532.3415702622165,"d":"-532.34"},{"v":1457.6172976151606,"d":"1457.62"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-4119.325148926243,"d":"-4119.33"},{"v":-187.24205222392013,"d":"-187.24"},{"v":-187.24205222392013,"d":"-187.24"}]
[19,3707.6471430461506,9.463000000000001,{"v":0,"d":"0.00"},{"v":-3575.1001021177176,"d":"-3575.10"},{"v":5.473000000000001,"d":"5.473"},{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":98.42579222714357,"d":"98.43"},{"v":268.4616683134062,"d":"268.46"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":289.2844876404073,"d":"289.28"},{"v":13.149294892745786,"d":"13.15"},{"v":13.149294892745786,"d":"13.15"}]
[20,3808.781241452949,5.473000000000001,{"v":0,"d":"0.00"},{"v":-3658.6494729837323,"d":"-3658.65"},{"v":13.322000000000001,"d":"13.322"},{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":231.1392860131259,"d":"231.14"},{"v":-479.53348935135335,"d":"-479.53"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1789.322776759067,"d":"1789.32"},{"v":81.3328534890485,"d":"81.33"},{"v":41.320621513081136,"d":"41.32"}]
[21,4004.179600353816,13.322000000000001,{"v":0,"d":"0.00"},{"v":-3840.969614883891,"d":"-3840.97"},{"v":24.51,"d":"24.510"},0.28,{"v":1.7,"d":"1.70"},{"v":401.33671391221696,"d":"401.34"},{"v":-670.4788224999638,"d":"-670.48"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3107.1660141098523,"d":"3107.17"},{"v":141.23481882317512,"d":"141.23"},{"v":69.28075591871642,"d":"69.28"}]
[22,4085.969865557809,24.51,{"v":0,"d":"0.00"},{"v":-4016.414529782343,"d":"-4016.41"},{"v":25.807000000000002,"d":"25.807"},{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":101.90709342149512,"d":"101.91"},{"v":-53.41789517377447,"d":"-53.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":630.8914245622468,"d":"630.89"},{"v":28.676882934647583,"d":"28.68"},{"v":28.676882934647583,"d":"28.68"}]
[23,4316.61711752646,25.807000000000002,{"v":0,"d":"0.00"},{"v":-4223.550184498671,"d":"-4223.55"},{"v":25.807000000000002,"d":"25.807"},{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":83.7942067806448,"d":"83.79"},{"v":40.496727438170865,"d":"40.50"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":434.337110985483,"d":"434.34"},{"v":19.74259595388559,"d":"19.74"},{"v":19.74259595388559,"d":"19.74"}]
[24,4685.403348294881,25.807000000000002,{"v":0,"d":"0.00"},{"v":-4524.995915458441,"d":"-4525.00"},26.844,{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":180.70863909465015,"d":"180.71"},{"v":-3.575730961658337,"d":"-3.58"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1027.5913524980092,"d":"1027.59"},{"v":46.7086978408186,"d":"46.71"},{"v":23.730046863647978,"d":"23.73"}]
[25,4935.5521658782945,26.844,{"v":0,"d":"0.00"},{"v":-4798.721678968049,"d":"-4798.72"},21.158,{"v":0.3,"d":"0.30"},{"v":1.5,"d":"1.50"},{"v":-71.33460296314024,"d":"-71.33"},{"v":496.44827062275476,"d":"496.45"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-853.121285438456,"d":"-853.12"},{"v":-38.77824024720255,"d":"-38.78"},{"v":-38.77824024720255,"d":"-38.78"}]
[26,5168.2874536593345,21.158,{"v":0,"d":"0.00"},{"v":-5018.790478569542,"d":"-5018.79"},{"v":19.194000000000003,"d":"19.194"},{"v":0.3,"d":"0.30"},{"v":1.7,"d":"1.70"},{"v":80.15518059481838,"d":"80.16"},{"v":215.3332471171277,"d":"215.33"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":238.87944292017642,"d":"238.88"},{"v":10.858156496371656,"d":"10.86"},{"v":10.858156496371656,"d":"10.86"}]
[27,5282.884845748546,19.194000000000003,{"v":26.732,"d":"26.73"},{"v":-5250.164896956906,"d":"-5250.16"},{"v":29.943000000000005,"d":"29.943"},0.35,{"v":1.5,"d":"1.50"},{"v":925.2559835590009,"d":"925.26"},{"v":-883.3576276183146,"d":"-883.36"},{"v":-2045.7459092285555,"d":"-2045.75"},{"v":2245.2561012581846,"d":"2245.26"},{"v":10505.883775867676,"d":"10505.88"},{"v":477.54017163034894,"d":"477.54"},{"v":127.49631689283207,"d":"127.50"}]
[28,4762.679527428672,29.943000000000005,{"v":58.31892,"d":"58.32"},{"v":-2077.5172743925687,"d":"-2077.52"},{"v":0,"d":"0.000"},{"v":0.7,"d":"0.70"},{"v":1.5,"d":"1.50"},{"v":3035.5933227311334,"d":"3035.59"},{"v":2376.141803181657,"d":"2376.14"},{"v":-1767.3719197311943,"d":"-1767.37"},{"v":3512.610186693674,"d":"3512.61"},{"v":5150.880025447646,"d":"5150.88"},{"v":234.13091024762028,"d":"234.13"},{"v":138.32295061641963,"d":"138.32"}]
["28'"]
[29,2742.8795062854797,29.943,{"v":55,"d":"55.00"},{"v":-2077.9871727008954,"d":"-2077.99"},{"v":0,"d":"0.000"},0.55,{"v":1.5,"d":"1.50"},{"v":1184.4164572181576,"d":"1184.42"},{"v":1368.4461905195446,"d":"1368.45"},{"v":-1701.6072153777109,"d":"-1701.61"},{"v":2073.2364697628436,"d":"2073.24"},{"v":4285.835090651846,"d":"4285.84"},{"v":194.8106859387203,"d":"194.81"},{"v":58.03596650217139,"d":"58.04"}]
[{"$nulls":13},{"v":1559.1175013228758,"d":"1559.12"}]